## All
stage | rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
Proposed_metrics | 1 | Swing_period1s_max_MW_x_Prms_MW | 64 | 0.9888 | 0 | 0.9256 | 0 | p<0.01 | 1
Proposed_metrics | 2 | Swing_period1s_max_MW_x_E_MJ | 64 | 0.9876 | 0 | 0.9226 | 0 | p<0.01 | 2.5
Proposed_metrics | 3 | Swing_period5s_max_MW | 64 | 0.9887 | 0 | 0.9216 | 0 | p<0.01 | 2.5
Proposed_metrics | 4 | Damage_proxy_per_h | 64 | 0.9867 | 0 | 0.9167 | 0 | p<0.01 | 4.25
Proposed_metrics | 5 | Swing_p95_p05_MW | 64 | 0.9865 | 0 | 0.9137 | 0 | p<0.01 | 5.75
Proposed_metrics | 6 | Max_change_in_1s_MW | 64 | 0.9864 | 0 | 0.9137 | 0 | p<0.01 | 6.25
Proposed_metrics | 7 | Swing_period1s_max_MW | 64 | 0.9867 | 0 | 0.9097 | 0 | p<0.01 | 6.75
Proposed_metrics | 8 | Power_cycle_dP_max_MW | 64 | 0.9862 | 0 | 0.9117 | 0 | p<0.01 | 7.5
Proposed_metrics | 9 | Swing_period10s_max_MW | 64 | 0.9861 | 0 | 0.9097 | 0 | p<0.01 | 9
Proposed_metrics | 10 | Swing_period60s_max_MW | 64 | 0.9858 | 0 | 0.9097 | 0 | p<0.01 | 9.75
Proposed_metrics | 11 | Max_change_in_60s_MW | 64 | 0.9858 | 0 | 0.9058 | 0 | p<0.01 | 11.25
Proposed_metrics | 12 | Swing_filtered_tau0.26s_MW | 64 | 0.9834 | 0 | 0.9087 | 0 | p<0.01 | 12
Proposed_metrics | 13 | Swing_period60s_median_MW | 64 | 0.9842 | 0 | 0.8988 | 0 | p<0.01 | 12.5
Proposed_metrics | 14 | Swing_period5s_max_MW_x_Prms_MW | 64 | 0.9823 | 0 | 0.8978 | 0 | p<0.01 | 14
Proposed_metrics | 15 | P_max_MW | 64 | 0.977 | 0 | 0.8956 | 0 | p<0.01 | 16.5
Proposed_metrics | 16 | Swing_period60s_mean_MW | 64 | 0.9796 | 0 | 0.8859 | 0 | p<0.01 | 16.5
Proposed_metrics | 17 | Swing_avg_1s_MW | 64 | 0.9771 | 0 | 0.8869 | 0 | p<0.01 | 17
Proposed_metrics | 18 | Swing_period5s_max_MW_x_E_MJ | 64 | 0.9775 | 0 | 0.8829 | 0 | p<0.01 | 17.5
Proposed_metrics | 19 | P_p999_MW | 64 | 0.975 | 0 | 0.8889 | 0 | p<0.01 | 17.5
Proposed_metrics | 20 | Step_height_pct_rating | 64 | 0.9729 | 0 | 0.871 | 0 | p<0.01 | 20.5
Proposed_metrics | 21 | Step_height_MW | 64 | 0.9729 | 0 | 0.871 | 0 | p<0.01 | 20.5
Proposed_metrics | 22 | Swing_period60s_max_MW_x_Prms_MW | 64 | 0.969 | 0 | 0.8671 | 0 | p<0.01 | 22
Proposed_metrics | 23 | Swing_period60s_median_MW_x_Prms_MW | 64 | 0.9661 | 0 | 0.8522 | 0 | p<0.01 | 23
Proposed_metrics | 24 | Swing_period10s_max_MW_x_Prms_MW | 64 | 0.9604 | 0 | 0.8452 | 0 | p<0.01 | 24
Proposed_metrics | 25 | Swing_period60s_mean_MW_x_Prms_MW | 64 | 0.9598 | 0 | 0.8363 | 0 | p<0.01 | 25.5
Proposed_metrics | 26 | P_high_level_MW | 64 | 0.9541 | 0 | 0.8373 | 0 | p<0.01 | 25.5
Proposed_metrics | 27 | Swing_period60s_max_MW_x_E_MJ | 64 | 0.9462 | 0 | 0.8185 | 0 | p<0.01 | 27
Proposed_metrics | 28 | Swing_period10s_max_MW_x_E_MJ | 64 | 0.9431 | 0 | 0.8105 | 0 | p<0.01 | 28
Proposed_metrics | 29 | Swing_period60s_median_MW_x_E_MJ | 64 | 0.9348 | 0 | 0.7986 | 0 | p<0.01 | 29
Proposed_metrics | 30 | Swing_period60s_mean_MW_x_E_MJ | 64 | 0.9208 | 0 | 0.7738 | 0 | p<0.01 | 30
Proposed_metrics | 31 | Power_cycles_ge_50pct_per_h | 64 | 0.853 | 0 | 0.6702 | 0 | p<0.01 | 31.5
Proposed_metrics | 32 | P_rms_MW | 64 | 0.8329 | 0 | 0.6677 | 0 | p<0.01 | 32.5
Proposed_metrics | 33 | Swing_period10s_mean_MW_x_Prms_MW | 64 | 0.7828 | 0 | 0.6657 | 0 | p<0.01 | 33.5
Proposed_metrics | 34 | Swing_period10s_median_MW | 64 | 0.7082 | 0 | 0.6806 | 0 | p<0.01 | 34
Proposed_metrics | 35 | Swing_period10s_mean_MW_x_E_MJ | 64 | 0.7596 | 0 | 0.631 | 0 | p<0.01 | 35
Proposed_metrics | 36 | Ramp_p99_MW_per_s | 64 | 0.7793 | 0 | 0.62 | 0 | p<0.01 | 35
Proposed_metrics | 37 | Swing_period10s_mean_MW | 64 | 0.7088 | 0 | 0.5913 | 0 | p<0.01 | 37
Proposed_metrics | 38 | Swing_period10s_median_MW_x_Prms_MW | 64 | 0.6786 | 0 | 0.6062 | 0 | p<0.01 | 39.5
Proposed_metrics | 39 | Swing_period5s_mean_MW_x_Prms_MW | 64 | 0.6909 | 0 | 0.5298 | 0 | p<0.01 | 40
Proposed_metrics | 40 | P_max_avg_60s_MW | 64 | 0.6969 | 0 | 0.5198 | 0 | p<0.01 | 40
Proposed_metrics | 41 | P_max_avg_180s_MW | 64 | 0.6917 | 0 | 0.5149 | 0 | p<0.01 | 41
Proposed_metrics | 42 | Swing_period5s_mean_MW_x_E_MJ | 64 | 0.6859 | 0 | 0.5268 | 0 | p<0.01 | 41
Proposed_metrics | 43 | Swing_period10s_median_MW_x_E_MJ | 64 | 0.6598 | 0 | 0.5685 | 0 | p<0.01 | 41.5
Proposed_metrics | 44 | Swing_filtered_tau3.31s_MW | 64 | 0.6729 | 0 | 0.5069 | 0 | p<0.01 | 43.5
Proposed_metrics | 45 | Swing_period1s_mean_MW_x_Prms_MW | 64 | 0.6166 | 0 | 0.4673 | 0 | p<0.01 | 45
Proposed_metrics | 46 | Swing_period1s_mean_MW_x_E_MJ | 64 | 0.6153 | 0 | 0.4653 | 0 | p<0.01 | 46.5
Proposed_metrics | 47 | P_low_level_MW | 64 | 0.6154 | 0 | 0.4613 | 0 | p<0.01 | 46.5
Proposed_metrics | 48 | P_max_avg_300s_MW | 64 | 0.6003 | 0 | 0.4454 | 0 | p<0.01 | 48
Proposed_metrics | 49 | P_min_MW | 64 | 0.5803 | 0 | 0.4226 | 0 | p<0.01 | 49.25
Proposed_metrics | 50 | Swing_period5s_mean_MW | 64 | 0.5701 | 0 | 0.4226 | 0 | p<0.01 | 49.75
Proposed_metrics | 51 | Energy_MWh | 64 | 0.5538 | 0 | 0.4129 | 0 | p<0.01 | 51.5
Proposed_metrics | 52 | P_mean_MW | 64 | 0.5538 | 0 | 0.4129 | 0 | p<0.01 | 51.5
Proposed_metrics | 53 | Swing_period5s_median_MW_x_E_MJ | 64 | 0.45 | 0.0002 | 0.372 | 0 | p<0.01 | 53
Proposed_metrics | 54 | Swing_period5s_median_MW_x_Prms_MW | 64 | 0.4319 | 0.0004 | 0.3522 | 0 | p<0.01 | 54.5
Proposed_metrics | 55 | Swing_period1s_mean_MW | 64 | 0.4471 | 0.0002 | 0.3254 | 0.0001 | p<0.01 | 55
Proposed_metrics | 56 | Swing_period5s_median_MW | 64 | 0.3995 | 0.0011 | 0.3363 | 0.0001 | p<0.01 | 55.5
Proposed_metrics | 57 | Peak_to_mean | 64 | 0.3653 | 0.003 | 0.2851 | 0.0009 | p<0.01 | 57
Proposed_metrics | 58 | Swing_filtered_tau159s_MW | 64 | 0.337 | 0.0065 | 0.249 | 0.0036 | p<0.01 | 58
Proposed_metrics | 59 | Time_at_high_load_pct | 64 | -0.3231 | 0.0092 | -0.24 | 0.0054 | p<0.01 | 59
Proposed_metrics | 60 | Power_cycles_ge_30pct_per_h | 64 | 0.307 | 0.0136 | 0.2127 | 0.0139 | p<0.05 | 60
Proposed_metrics | 61 | Swing_period1s_median_MW_x_E_MJ | 64 | 0.2487 | 0.0475 | 0.1954 | 0.0224 | p<0.05 | 61
Proposed_metrics | 62 | Swing_period1s_median_MW_x_Prms_MW | 64 | 0.2474 | 0.0487 | 0.1935 | 0.0239 | p<0.05 | 62
Proposed_metrics | 63 | Dwell_high_mean_s | 64 | -0.1851 | 0.143 | -0.128 | 0.1378 | - | 63.5
Proposed_metrics | 64 | Swing_period1s_median_MW | 64 | 0.1815 | 0.1513 | 0.1339 | 0.1178 | - | 64.5
Proposed_metrics | 65 | Dwell_high_p95_s | 64 | -0.1845 | 0.1444 | -0.126 | 0.1441 | - | 65
Proposed_metrics | 66 | Power_cycles_ge_10pct_per_h | 64 | 0.1824 | 0.1491 | 0.1276 | 0.1379 | - | 65
Proposed_metrics | 67 | Transitions_per_h | 64 | 0.1365 | 0.2821 | 0.0992 | 0.251 | - | 67.5
Proposed_metrics | 68 | Bursts_per_h | 64 | 0.1365 | 0.2821 | 0.0992 | 0.251 | - | 67.5
Proposed_metrics | 69 | Burst_period_mean_s | 64 | -0.1337 | 0.292 | -0.098 | 0.2559 | - | 69
Proposed_metrics | 70 | Dwell_low_mean_s | 64 | 0.0994 | 0.4346 | 0.08 | 0.3537 | - | 70
Proposed_metrics | 71 | Dominant_period_s | 64 | -0.0961 | 0.4502 | -0.0794 | 0.3594 | - | 71
Proposed_metrics | 72 | Dwell_low_p95_s | 64 | 0.0471 | 0.7114 | 0.0422 | 0.6262 | - | 72
Proposed_metrics | 73 | Burst_period_CV | 64 | 0.0392 | 0.7584 | 0.022 | 0.7987 | - | 73
Grid_operator_metrics | 1 | Max_change_in_5s_MW | 64 | 0.9857 | 0 | 0.9067 | 0 | p<0.01 | 1
Grid_operator_metrics | 2 | SoCo_band_0.1_0.5Hz_amp_60s_MW | 64 | 0.7919 | 0 | 0.6181 | 0 | p<0.01 | 2
Grid_operator_metrics | 3 | SoCo_band_0.5_0.8Hz_amp_60s_MW | 64 | 0.7088 | 0 | 0.5496 | 0 | p<0.01 | 3
Grid_operator_metrics | 4 | Swing_avg_4s_MW | 64 | 0.7009 | 0 | 0.5347 | 0 | p<0.01 | 4
Grid_operator_metrics | 5 | Max_change_in_0.1s_MW | 64 | 0.4349 | 0.0003 | 0.3056 | 0.0004 | p<0.01 | 5
Grid_operator_metrics | 6 | SoCo_band_0.8_2Hz_amp_60s_MW | 64 | 0.4037 | 0.0009 | 0.2837 | 0.0009 | p<0.01 | 6
Grid_operator_metrics | 7 | LIPA_band_5_23.75Hz_amp_10s_MW | 64 | 0.4003 | 0.001 | 0.2738 | 0.0014 | p<0.01 | 7
Grid_operator_metrics | 8 | Swing_avg_60s_MW | 64 | 0.3452 | 0.0052 | 0.255 | 0.0029 | p<0.01 | 8
Grid_operator_metrics | 9 | Ramp_max_MW_per_min | 64 | 0.3423 | 0.0056 | 0.254 | 0.003 | p<0.01 | 9
Grid_operator_metrics | 10 | Swing_avg_300s_MW | 64 | 0.2582 | 0.0394 | 0.1925 | 0.0246 | p<0.05 | 10
Grid_operator_metrics | 11 | ERCOT_changes_gt25pct_in_5s_per_h | 64 | 0.2395 | 0.0567 | 0.1753 | 0.0429 | - | 11
Electrical | 1 | P_loss_IGBT_swing_W | 64 | 0.9905 | 0 | 0.9306 | 0 | p<0.01 | 1
Electrical | 2 | I_IGBT_rms_A | 64 | 0.8329 | 0 | 0.6677 | 0 | p<0.01 | 2
Electrical | 3 | P_loss_IGBT_mean_W | 64 | 0.749 | 0 | 0.6042 | 0 | p<0.01 | 3
Thermal | 1 | IGBT_burst_dT_eq_K | 59 | 0.9821 | 0 | 0.9088 | 0 | p<0.01 | 1
Thermal | 2 | IGBT_burst_Tmean_C | 59 | 0.712 | 0 | 0.5488 | 0 | p<0.01 | 2
Thermal | 3 | IGBT_burst_duration_mean_s | 59 | -0.0504 | 0.7046 | -0.0339 | 0.7045 | - | 3

## Proposed_metrics
rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
1 | Swing_period1s_max_MW_x_Prms_MW | 64 | 0.9888 | 0 | 0.9256 | 0 | p<0.01 | 1
2 | Swing_period1s_max_MW_x_E_MJ | 64 | 0.9876 | 0 | 0.9226 | 0 | p<0.01 | 2.5
3 | Swing_period5s_max_MW | 64 | 0.9887 | 0 | 0.9216 | 0 | p<0.01 | 2.5
4 | Damage_proxy_per_h | 64 | 0.9867 | 0 | 0.9167 | 0 | p<0.01 | 4.25
5 | Swing_p95_p05_MW | 64 | 0.9865 | 0 | 0.9137 | 0 | p<0.01 | 5.75
6 | Max_change_in_1s_MW | 64 | 0.9864 | 0 | 0.9137 | 0 | p<0.01 | 6.25
7 | Swing_period1s_max_MW | 64 | 0.9867 | 0 | 0.9097 | 0 | p<0.01 | 6.75
8 | Power_cycle_dP_max_MW | 64 | 0.9862 | 0 | 0.9117 | 0 | p<0.01 | 7.5
9 | Swing_period10s_max_MW | 64 | 0.9861 | 0 | 0.9097 | 0 | p<0.01 | 9
10 | Swing_period60s_max_MW | 64 | 0.9858 | 0 | 0.9097 | 0 | p<0.01 | 9.75
11 | Max_change_in_60s_MW | 64 | 0.9858 | 0 | 0.9058 | 0 | p<0.01 | 11.25
12 | Swing_filtered_tau0.26s_MW | 64 | 0.9834 | 0 | 0.9087 | 0 | p<0.01 | 12
13 | Swing_period60s_median_MW | 64 | 0.9842 | 0 | 0.8988 | 0 | p<0.01 | 12.5
14 | Swing_period5s_max_MW_x_Prms_MW | 64 | 0.9823 | 0 | 0.8978 | 0 | p<0.01 | 14
15 | P_max_MW | 64 | 0.977 | 0 | 0.8956 | 0 | p<0.01 | 16.5
16 | Swing_period60s_mean_MW | 64 | 0.9796 | 0 | 0.8859 | 0 | p<0.01 | 16.5
17 | Swing_avg_1s_MW | 64 | 0.9771 | 0 | 0.8869 | 0 | p<0.01 | 17
18 | Swing_period5s_max_MW_x_E_MJ | 64 | 0.9775 | 0 | 0.8829 | 0 | p<0.01 | 17.5
19 | P_p999_MW | 64 | 0.975 | 0 | 0.8889 | 0 | p<0.01 | 17.5
20 | Step_height_pct_rating | 64 | 0.9729 | 0 | 0.871 | 0 | p<0.01 | 20.5
21 | Step_height_MW | 64 | 0.9729 | 0 | 0.871 | 0 | p<0.01 | 20.5
22 | Swing_period60s_max_MW_x_Prms_MW | 64 | 0.969 | 0 | 0.8671 | 0 | p<0.01 | 22
23 | Swing_period60s_median_MW_x_Prms_MW | 64 | 0.9661 | 0 | 0.8522 | 0 | p<0.01 | 23
24 | Swing_period10s_max_MW_x_Prms_MW | 64 | 0.9604 | 0 | 0.8452 | 0 | p<0.01 | 24
25 | Swing_period60s_mean_MW_x_Prms_MW | 64 | 0.9598 | 0 | 0.8363 | 0 | p<0.01 | 25.5
26 | P_high_level_MW | 64 | 0.9541 | 0 | 0.8373 | 0 | p<0.01 | 25.5
27 | Swing_period60s_max_MW_x_E_MJ | 64 | 0.9462 | 0 | 0.8185 | 0 | p<0.01 | 27
28 | Swing_period10s_max_MW_x_E_MJ | 64 | 0.9431 | 0 | 0.8105 | 0 | p<0.01 | 28
29 | Swing_period60s_median_MW_x_E_MJ | 64 | 0.9348 | 0 | 0.7986 | 0 | p<0.01 | 29
30 | Swing_period60s_mean_MW_x_E_MJ | 64 | 0.9208 | 0 | 0.7738 | 0 | p<0.01 | 30
31 | Power_cycles_ge_50pct_per_h | 64 | 0.853 | 0 | 0.6702 | 0 | p<0.01 | 31.5
32 | P_rms_MW | 64 | 0.8329 | 0 | 0.6677 | 0 | p<0.01 | 32.5
33 | Swing_period10s_mean_MW_x_Prms_MW | 64 | 0.7828 | 0 | 0.6657 | 0 | p<0.01 | 33.5
34 | Swing_period10s_median_MW | 64 | 0.7082 | 0 | 0.6806 | 0 | p<0.01 | 34
35 | Swing_period10s_mean_MW_x_E_MJ | 64 | 0.7596 | 0 | 0.631 | 0 | p<0.01 | 35
36 | Ramp_p99_MW_per_s | 64 | 0.7793 | 0 | 0.62 | 0 | p<0.01 | 35
37 | Swing_period10s_mean_MW | 64 | 0.7088 | 0 | 0.5913 | 0 | p<0.01 | 37
38 | Swing_period10s_median_MW_x_Prms_MW | 64 | 0.6786 | 0 | 0.6062 | 0 | p<0.01 | 39.5
39 | Swing_period5s_mean_MW_x_Prms_MW | 64 | 0.6909 | 0 | 0.5298 | 0 | p<0.01 | 40
40 | P_max_avg_60s_MW | 64 | 0.6969 | 0 | 0.5198 | 0 | p<0.01 | 40
41 | P_max_avg_180s_MW | 64 | 0.6917 | 0 | 0.5149 | 0 | p<0.01 | 41
42 | Swing_period5s_mean_MW_x_E_MJ | 64 | 0.6859 | 0 | 0.5268 | 0 | p<0.01 | 41
43 | Swing_period10s_median_MW_x_E_MJ | 64 | 0.6598 | 0 | 0.5685 | 0 | p<0.01 | 41.5
44 | Swing_filtered_tau3.31s_MW | 64 | 0.6729 | 0 | 0.5069 | 0 | p<0.01 | 43.5
45 | Swing_period1s_mean_MW_x_Prms_MW | 64 | 0.6166 | 0 | 0.4673 | 0 | p<0.01 | 45
46 | Swing_period1s_mean_MW_x_E_MJ | 64 | 0.6153 | 0 | 0.4653 | 0 | p<0.01 | 46.5
47 | P_low_level_MW | 64 | 0.6154 | 0 | 0.4613 | 0 | p<0.01 | 46.5
48 | P_max_avg_300s_MW | 64 | 0.6003 | 0 | 0.4454 | 0 | p<0.01 | 48
49 | P_min_MW | 64 | 0.5803 | 0 | 0.4226 | 0 | p<0.01 | 49.25
50 | Swing_period5s_mean_MW | 64 | 0.5701 | 0 | 0.4226 | 0 | p<0.01 | 49.75
51 | Energy_MWh | 64 | 0.5538 | 0 | 0.4129 | 0 | p<0.01 | 51.5
52 | P_mean_MW | 64 | 0.5538 | 0 | 0.4129 | 0 | p<0.01 | 51.5
53 | Swing_period5s_median_MW_x_E_MJ | 64 | 0.45 | 0.0002 | 0.372 | 0 | p<0.01 | 53
54 | Swing_period5s_median_MW_x_Prms_MW | 64 | 0.4319 | 0.0004 | 0.3522 | 0 | p<0.01 | 54.5
55 | Swing_period1s_mean_MW | 64 | 0.4471 | 0.0002 | 0.3254 | 0.0001 | p<0.01 | 55
56 | Swing_period5s_median_MW | 64 | 0.3995 | 0.0011 | 0.3363 | 0.0001 | p<0.01 | 55.5
57 | Peak_to_mean | 64 | 0.3653 | 0.003 | 0.2851 | 0.0009 | p<0.01 | 57
58 | Swing_filtered_tau159s_MW | 64 | 0.337 | 0.0065 | 0.249 | 0.0036 | p<0.01 | 58
59 | Time_at_high_load_pct | 64 | -0.3231 | 0.0092 | -0.24 | 0.0054 | p<0.01 | 59
60 | Power_cycles_ge_30pct_per_h | 64 | 0.307 | 0.0136 | 0.2127 | 0.0139 | p<0.05 | 60
61 | Swing_period1s_median_MW_x_E_MJ | 64 | 0.2487 | 0.0475 | 0.1954 | 0.0224 | p<0.05 | 61
62 | Swing_period1s_median_MW_x_Prms_MW | 64 | 0.2474 | 0.0487 | 0.1935 | 0.0239 | p<0.05 | 62
63 | Dwell_high_mean_s | 64 | -0.1851 | 0.143 | -0.128 | 0.1378 | - | 63.5
64 | Swing_period1s_median_MW | 64 | 0.1815 | 0.1513 | 0.1339 | 0.1178 | - | 64.5
65 | Dwell_high_p95_s | 64 | -0.1845 | 0.1444 | -0.126 | 0.1441 | - | 65
66 | Power_cycles_ge_10pct_per_h | 64 | 0.1824 | 0.1491 | 0.1276 | 0.1379 | - | 65
67 | Transitions_per_h | 64 | 0.1365 | 0.2821 | 0.0992 | 0.251 | - | 67.5
68 | Bursts_per_h | 64 | 0.1365 | 0.2821 | 0.0992 | 0.251 | - | 67.5
69 | Burst_period_mean_s | 64 | -0.1337 | 0.292 | -0.098 | 0.2559 | - | 69
70 | Dwell_low_mean_s | 64 | 0.0994 | 0.4346 | 0.08 | 0.3537 | - | 70
71 | Dominant_period_s | 64 | -0.0961 | 0.4502 | -0.0794 | 0.3594 | - | 71
72 | Dwell_low_p95_s | 64 | 0.0471 | 0.7114 | 0.0422 | 0.6262 | - | 72
73 | Burst_period_CV | 64 | 0.0392 | 0.7584 | 0.022 | 0.7987 | - | 73

## Grid_operator_metrics
rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
1 | Max_change_in_5s_MW | 64 | 0.9857 | 0 | 0.9067 | 0 | p<0.01 | 1
2 | SoCo_band_0.1_0.5Hz_amp_60s_MW | 64 | 0.7919 | 0 | 0.6181 | 0 | p<0.01 | 2
3 | SoCo_band_0.5_0.8Hz_amp_60s_MW | 64 | 0.7088 | 0 | 0.5496 | 0 | p<0.01 | 3
4 | Swing_avg_4s_MW | 64 | 0.7009 | 0 | 0.5347 | 0 | p<0.01 | 4
5 | Max_change_in_0.1s_MW | 64 | 0.4349 | 0.0003 | 0.3056 | 0.0004 | p<0.01 | 5
6 | SoCo_band_0.8_2Hz_amp_60s_MW | 64 | 0.4037 | 0.0009 | 0.2837 | 0.0009 | p<0.01 | 6
7 | LIPA_band_5_23.75Hz_amp_10s_MW | 64 | 0.4003 | 0.001 | 0.2738 | 0.0014 | p<0.01 | 7
8 | Swing_avg_60s_MW | 64 | 0.3452 | 0.0052 | 0.255 | 0.0029 | p<0.01 | 8
9 | Ramp_max_MW_per_min | 64 | 0.3423 | 0.0056 | 0.254 | 0.003 | p<0.01 | 9
10 | Swing_avg_300s_MW | 64 | 0.2582 | 0.0394 | 0.1925 | 0.0246 | p<0.05 | 10
11 | ERCOT_changes_gt25pct_in_5s_per_h | 64 | 0.2395 | 0.0567 | 0.1753 | 0.0429 | - | 11

## Electrical_characteristics
rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
1 | P_loss_IGBT_swing_W | 64 | 0.9905 | 0 | 0.9306 | 0 | p<0.01 | 1
2 | I_IGBT_rms_A | 64 | 0.8329 | 0 | 0.6677 | 0 | p<0.01 | 2
3 | P_loss_IGBT_mean_W | 64 | 0.749 | 0 | 0.6042 | 0 | p<0.01 | 3

## Thermal_characteristics
rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
1 | IGBT_burst_dT_eq_K | 59 | 0.9821 | 0 | 0.9088 | 0 | p<0.01 | 1
2 | IGBT_burst_Tmean_C | 59 | 0.712 | 0 | 0.5488 | 0 | p<0.01 | 2
3 | IGBT_burst_duration_mean_s | 59 | -0.0504 | 0.7046 | -0.0339 | 0.7045 | - | 3