## All_results
scenario | chip | duration_s | P_mean_MW | P_max_MW | P_min_MW | Energy_MWh | Peak_to_mean | Swing_p95_p05_MW | Time_at_high_load_pct | Dominant_period_s | Transitions_per_h | Ramp_p99_MW_per_s | P_high_level_MW | P_low_level_MW | Step_height_MW | Step_height_pct_rating | P_p999_MW | Dwell_high_mean_s | Dwell_high_p95_s | Dwell_low_mean_s | Dwell_low_p95_s | Bursts_per_h | Burst_period_mean_s | Burst_period_CV | Power_cycles_ge_10pct_per_h | Power_cycles_ge_30pct_per_h | Power_cycles_ge_50pct_per_h | Power_cycle_dP_max_MW | Damage_proxy_per_h | Swing_filtered_tau0.26s_MW | Swing_filtered_tau3.31s_MW | Swing_filtered_tau159s_MW | Max_change_in_0.1s_MW | Max_change_in_1s_MW | Max_change_in_5s_MW | Max_change_in_60s_MW | Swing_avg_1s_MW | Swing_avg_60s_MW | Swing_avg_900s_MW | Var_share_0_0.017Hz_pct | Var_share_0.017_0.1Hz_pct | Var_share_0.1_0.5Hz_pct | Var_share_0.5_0.8Hz_pct | Var_share_0.8_2Hz_pct | Var_share_2_25Hz_pct | Seam_jump_max_MW | Startup_60s_mean_minus_block_mean_MW | P_rms_MW | P_max_avg_60s_MW | P_max_avg_180s_MW | P_max_avg_300s_MW | Swing_period1s_max_MW | Swing_period1s_max_MW_x_E_MJ | Swing_period1s_max_MW_x_Prms_MW | Swing_period1s_mean_MW | Swing_period1s_mean_MW_x_E_MJ | Swing_period1s_mean_MW_x_Prms_MW | Swing_period1s_median_MW | Swing_period1s_median_MW_x_E_MJ | Swing_period1s_median_MW_x_Prms_MW | Swing_period5s_max_MW | Swing_period5s_max_MW_x_E_MJ | Swing_period5s_max_MW_x_Prms_MW | Swing_period5s_mean_MW | Swing_period5s_mean_MW_x_E_MJ | Swing_period5s_mean_MW_x_Prms_MW | Swing_period5s_median_MW | Swing_period5s_median_MW_x_E_MJ | Swing_period5s_median_MW_x_Prms_MW | Swing_period10s_max_MW | Swing_period10s_max_MW_x_E_MJ | Swing_period10s_max_MW_x_Prms_MW | Swing_period10s_mean_MW | Swing_period10s_mean_MW_x_E_MJ | Swing_period10s_mean_MW_x_Prms_MW | Swing_period10s_median_MW | Swing_period10s_median_MW_x_E_MJ | Swing_period10s_median_MW_x_Prms_MW | Swing_period60s_max_MW | Swing_period60s_max_MW_x_E_MJ | Swing_period60s_max_MW_x_Prms_MW | Swing_period60s_mean_MW | Swing_period60s_mean_MW_x_E_MJ | Swing_period60s_mean_MW_x_Prms_MW | Swing_period60s_median_MW | Swing_period60s_median_MW_x_E_MJ | Swing_period60s_median_MW_x_Prms_MW | ERCOT_changes_gt25pct_in_5s_per_h | LIPA_band_5_23.75Hz_amp_10s_MW | Ramp_max_MW_per_min | Variability_1min_std_MW | Swing_avg_4s_MW | Swing_avg_300s_MW | SoCo_band_0.1_0.5Hz_amp_60s_MW | SoCo_band_0.5_0.8Hz_amp_60s_MW | SoCo_band_0.8_2Hz_amp_60s_MW | Flicker_Pst_max_SCR20 | Peak_demand_15min_MW | Load_factor_15min | I_IGBT_rms_A | I_IGBT_peak_A | I_Diode_rms_A | I_Diode_peak_A | P_loss_IGBT_mean_W | P_loss_IGBT_max_W | P_loss_IGBT_swing_W | P_loss_Diode_mean_W | P_loss_Diode_max_W | P_loss_Diode_swing_W | Switching_share_pct | Diode_share_pct | Loss_ratio_pct | Tj_IGBT_mean_C | Tj_IGBT_max_C | Tj_IGBT_min_C | Tj_IGBT_swing_K | Tj_Diode_mean_C | Tj_Diode_max_C | Tj_Diode_min_C | Tj_Diode_swing_K | T_case_mean_C | T_case_swing_K | IGBT_cycles_per_h | IGBT_dT_max_K | IGBT_dT_mean_K | IGBT_dT_p95_K | IGBT_cycles_dT_lt5_per_h | IGBT_cycles_dT_5_10_per_h | IGBT_cycles_dT_10_20_per_h | IGBT_cycles_dT_ge20_per_h | IGBT_cycle_Tmean_C | IGBT_cycle_duration_mean_s | IGBT_cycle_duration_p95_s | IGBT_grid_cycles_per_h | IGBT_grid_cycle_dT_mean_K | IGBT_grid_cycle_dT_max_K | IGBT_load_cycles_per_h | IGBT_load_cycle_dT_mean_K | IGBT_load_cycle_dT_max_K | IGBT_load_cycle_Tmean_C | IGBT_load_cycle_duration_mean_s | IGBT_burst_cycles_per_h | IGBT_burst_dT_mean_K | IGBT_burst_dT_median_K | IGBT_burst_dT_p95_K | IGBT_burst_dT_max_K | IGBT_burst_dT_eq_K | IGBT_burst_Tmean_C | IGBT_burst_duration_mean_s | Diode_cycles_per_h | Diode_dT_max_K | Diode_dT_mean_K | Diode_dT_p95_K | Diode_cycles_dT_lt5_per_h | Diode_cycles_dT_5_10_per_h | Diode_cycles_dT_10_20_per_h | Diode_cycles_dT_ge20_per_h | Diode_cycle_Tmean_C | Diode_cycle_duration_mean_s | Diode_cycle_duration_p95_s | Diode_grid_cycles_per_h | Diode_grid_cycle_dT_mean_K | Diode_grid_cycle_dT_max_K | Diode_load_cycles_per_h | Diode_load_cycle_dT_mean_K | Diode_load_cycle_dT_max_K | Diode_load_cycle_Tmean_C | Diode_load_cycle_duration_mean_s | Diode_burst_cycles_per_h | Diode_burst_dT_mean_K | Diode_burst_dT_median_K | Diode_burst_dT_p95_K | Diode_burst_dT_max_K | Diode_burst_dT_eq_K | Diode_burst_Tmean_C | Diode_burst_duration_mean_s | Mission_duration_s | IGBT_Nf_eq | IGBT_Nf_eq_dT_ge10 | IGBT_Nf_eq_dT_lt10 | IGBT_Nf_eq_load_cycles | IGBT_Nf_eq_grid_cycles | IGBT_Nf_worst_cycle | IGBT_worst_cycle_dT_K | IGBT_worst_cycle_Tmean_C | Diode_Nf_eq | Diode_Nf_eq_dT_ge10 | Diode_Nf_eq_dT_lt10 | Diode_Nf_eq_load_cycles | Diode_Nf_eq_grid_cycles | Diode_Nf_worst_cycle | Diode_worst_cycle_dT_K | Diode_worst_cycle_Tmean_C | Limiting_device | IGBT_lifetime_years_actual | Diode_lifetime_years_actual
Image_H100_BatchSize_128 | H_100 | 3600 | 0.44828 | 0.86506 | 0.25337 | 0.44828 | 1.9298 | 0.58625 | 33.7089 | 16.0714 | 464 | 1.1514 | 0.81992 | 0.25577 | 0.56415 | 28.2077 | 0.86183 | 5.208 | 5.52 | 10.2948 | 11.213 | 231 | 15.5036 | 0.14852 | 232 | 24 | 0 | 0.60884 | 8.1173e-08 | 0.58469 | 0.40688 | 0.014932 | 0.16933 | 0.576 | 0.61062 | 0.61066 | 0.58385 | 0.039496 | 0 | 0.14094 | 76.0438 | 23.3736 | 0.37502 | 0.053716 | 0.012963 | 0.16758 | 0.0083248 | 0.51483 | 0.48853 | 0.46708 | 0.45534 | 0.51028 | 0.29333 | 0.30424 | 0.068075 | 0.037355 | 0.038272 | 0.0053346 | 0.0031312 | 0.0031314 | 0.60083 | 2.1948 | 0.45759 | 0.31942 | 0.86006 | 0.18525 | 0.39076 | 0.8852 | 0.19665 | 0.60856 | 3.368 | 0.37368 | 0.51323 | 2.4219 | 0.27197 | 0.57681 | 2.7095 | 0.30995 | 0.60222 | 16.4177 | 0.31328 | 0.58454 | 15.7244 | 0.30088 | 0.58338 | 15.927 | 0.30321 | 444 | 0.12854 | 0.037902 | 0.019296 | 0.55369 | 0.0012562 | 0.55703 | 0.10309 | 0.082359 | 0.2465 | 0.44828 | 1 | 237.0244 | 844.7903 | 70.2707 | 196.1497 | 186.7893 | 369.0614 | 255.0061 | 15.7291 | 30.835 | 21.1708 | 50.7192 | 7.7668 | 0.045177 | 78.4264 | 83.6663 | 25 | 15.0466 | 75.7382 | 78.2213 | 25 | 12.5157 | 75.1234 | 12.0646 | 180000.0417 | 58.6663 | 0.3991 | 0.76513 | 179971.0417 | 28.9583 | 0 | 0.041667 | 78.4363 | 0.055983 | 0.013 | 179068.4167 | 0.39241 | 0.78871 | 931.625 | 1.6854 | 58.6663 | 79.6042 | 9.0236 | 28.9583 | 5.0416 | 5.0301 | 5.1075 | 5.1075 | 5.0429 | 80.9657 | 130.6667 | 180000 | 53.2213 | 0.08733 | 0.16584 | 179999.9583 | 0 | 0 | 0.041667 | 75.7388 | 0.044723 | 0.012 | 179268.9583 | 0.086177 | 0.17095 | 731.0417 | 0.37009 | 53.2213 | 75.9027 | 8.6636 | 0 | [7 empty] | 43200 | 1925453.7447 | inf | 1925453.7447 | 1925453.7447 | 4.2275e+28 | 962726.8729 | 58.6663 | 54.3332 | 1668505.8208 | inf | 1668505.8208 | 1668505.8208 | 6.7466e+38 | 834252.9104 | 53.2213 | 51.6106 | Diode | 2637.6079 | 2285.6244
Image_H100_BatchSize_256 | H_100 | 3600 | 0.43236 | 0.65396 | 0.25349 | 0.43236 | 1.5125 | 0.39229 | 45.1533 | 18 | 399 | 0.74254 | 0.64305 | 0.2576 | 0.38545 | 19.2726 | 0.65241 | 8.1003 | 8.38 | 9.9176 | 10.52 | 199 | 18.0179 | 0.10673 | 199.5 | 0 | 0 | 0.39869 | 5.8653e-11 | 0.39173 | 0.31897 | 0.012861 | 0.38697 | 0.38934 | 0.3966 | 0.39942 | 0.39148 | 0.038684 | 0 | 0.12143 | 86.4639 | 12.9889 | 0.36003 | 0.042305 | 0.023434 | 0.38624 | -0.014306 | 0.46951 | 0.45982 | 0.43813 | 0.4409 | 0.32803 | 0.1543 | 0.1571 | 0.039842 | 0.018344 | 0.018611 | 0.0049797 | 0.0028382 | 0.0028384 | 0.39437 | 1.1313 | 0.23194 | 0.18918 | 0.42564 | 0.089371 | 0.1867 | 0.36917 | 0.076648 | 0.39489 | 2.2136 | 0.2288 | 0.36723 | 1.6185 | 0.17237 | 0.38886 | 1.6773 | 0.1821 | 0.39438 | 10.7768 | 0.19372 | 0.39205 | 10.1707 | 0.18401 | 0.39235 | 10.0601 | 0.18218 | 0 | 0.28828 | 0.037438 | 0.019181 | 0.3888 | 0.0069119 | 0.46534 | 0.11444 | 0.20768 | 0.19598 | 0.43236 | 1 | 216.1582 | 638.6349 | 64.0845 | 148.283 | 178.8793 | 273.9837 | 167.9054 | 15.0991 | 23.0295 | 14.0135 | 51.0723 | 7.7839 | 0.044865 | 76.1735 | 79.8514 | 25 | 13.2428 | 73.6005 | 75.7339 | 25 | 11.6974 | 73.0103 | 11.4266 | 180000.0417 | 54.8514 | 0.38193 | 0.57945 | 180000 | 0 | 0 | 0.041667 | 76.1828 | 0.04776 | 0.013 | 177100.7917 | 0.37618 | 0.59064 | 2899.25 | 0.7328 | 54.8514 | 77.4792 | 2.3598 | 0 | [7 empty] | 180000 | 50.7339 | 0.083814 | 0.1264 | 179999.9583 | 0 | 0 | 0.041667 | 73.6011 | 0.040859 | 0.012 | 178318.125 | 0.083018 | 0.12811 | 1681.875 | 0.16814 | 50.7339 | 74.5362 | 3.2861 | 0 | [7 empty] | 43200 | 2808296.3504 | inf | 2808296.3504 | 2808296.3504 | 2.5084e+30 | 1404148.1752 | 54.8514 | 52.4257 | 2204463.8062 | inf | 2204463.8062 | 2204463.8062 | 2.5847e+40 | 1102231.9031 | 50.7339 | 50.3669 | Diode | 3846.9813 | 3019.8134
Image_H100_BatchSize_512 | H_100 | 3600 | 0.45261 | 1.1269 | 0.25307 | 0.45261 | 2.4897 | 0.85156 | 16.4356 | 14.0625 | 312 | 1.5462 | 1.1027 | 0.25847 | 0.84418 | 42.209 | 1.1243 | 3.32 | 3.34 | 17.5289 | 11 | 156 | 20.849 | 2.3419 | 243.5 | 156 | 0 | 0.86546 | 4.8191e-05 | 0.84731 | 0.44267 | 0.028347 | 0.63706 | 0.80482 | 0.87039 | 0.8734 | 0.84756 | 0.078641 | 0 | 0.24609 | 64.7699 | 34.2835 | 0.57758 | 0.078517 | 0.044399 | 0.41727 | -0.023391 | 0.53491 | 0.49933 | 0.47211 | 0.46975 | 0.74447 | 0.5535 | 0.57775 | 0.0884 | 0.057094 | 0.058843 | 0.01732 | 0.0063819 | 0.0063841 | 0.86424 | 3.5248 | 0.76065 | 0.37895 | 1.0998 | 0.24595 | 0.36296 | 0.67557 | 0.14309 | 0.86485 | 4.7121 | 0.56531 | 0.60892 | 2.9098 | 0.34146 | 0.59652 | 2.3787 | 0.24792 | 0.86191 | 25.2749 | 0.51628 | 0.68418 | 18.7906 | 0.37459 | 0.85502 | 23.0557 | 0.47411 | 156 | 0.47513 | 0.078641 | 0.031173 | 0.62119 | 0.028582 | 0.77105 | 0.18355 | 0.34052 | 0.45861 | 0.45261 | 1 | 246.2676 | 1100.4691 | 73.011 | 255.5151 | 189.2689 | 491.4769 | 378.7234 | 15.9189 | 40.7672 | 31.217 | 50.5436 | 7.7582 | 0.045334 | 79.1215 | 86.7809 | 25 | 17.1014 | 76.3968 | 79.4821 | 25 | 13.2815 | 75.7746 | 12.7118 | 180000.0417 | 61.7809 | 0.40454 | 1.0305 | 179844.0417 | 155.9583 | 0 | 0.041667 | 79.1315 | 0.04065 | 0.013 | 177903.7917 | 0.39346 | 1.0582 | 2096.25 | 1.345 | 61.7809 | 81.1841 | 2.7203 | 155.9583 | 7.1291 | 7.1321 | 7.2095 | 7.7543 | 7.1454 | 81.3396 | 17.3802 | 180000.1667 | 54.4821 | 0.088394 | 0.22177 | 180000.125 | 0 | 0 | 0.041667 | 76.3974 | 0.041126 | 0.012 | 177786.3333 | 0.086447 | 0.22839 | 2213.8333 | 0.24474 | 54.4821 | 76.9568 | 2.5791 | 0 | [7 empty] | 43200 | 1447711.0638 | inf | 1447711.0638 | 1447711.0638 | 6.6208e+26 | 723855.7163 | 61.7809 | 55.8904 | 1459168.9029 | inf | 1459168.9029 | 1459168.9029 | 1.6449e+37 | 729584.4514 | 54.4821 | 52.241 | IGBT | 1983.1658 | 1998.8615
Image_H100_ImageSize_16 | H_100 | 3600 | 0.36404 | 0.59557 | 0.25435 | 0.36404 | 1.636 | 0.32806 | 32.7044 | 12 | 599 | 0.62063 | 0.57686 | 0.25958 | 0.31728 | 15.864 | 0.59264 | 3.9323 | 4.16 | 8.0807 | 8.68 | 299 | 12.013 | 0.040278 | 299.5 | 0 | 0 | 0.33837 | 3.5755e-12 | 0.32649 | 0.18779 | 0.0066814 | 0.29585 | 0.32174 | 0.33639 | 0.33748 | 0.32552 | 0.0093232 | 0 | 0.12879 | 76.108 | 22.97 | 0.67663 | 0.093389 | 0.023176 | 0.26885 | -0.0013946 | 0.3897 | 0.36847 | 0.36601 | 0.36578 | 0.28686 | 0.12514 | 0.12789 | 0.049555 | 0.021045 | 0.021355 | 0.0030189 | 0.00095465 | 0.00095466 | 0.33272 | 0.83999 | 0.17219 | 0.22622 | 0.45857 | 0.095986 | 0.31666 | 0.57781 | 0.12261 | 0.33322 | 1.29 | 0.13804 | 0.32447 | 1.1815 | 0.12615 | 0.32536 | 1.2319 | 0.13159 | 0.33101 | 7.2414 | 0.1292 | 0.32754 | 7.1541 | 0.12764 | 0.32766 | 7.1602 | 0.12767 | 0 | 0.198 | 0.0069867 | 0.0033992 | 0.27873 | 0.0028278 | 0.27628 | 0.11906 | 0.17748 | 0.17125 | 0.36404 | 1 | 179.4119 | 581.6134 | 53.1903 | 135.0433 | 149.3872 | 248.2574 | 139.7113 | 12.6446 | 20.9026 | 11.6797 | 51.4803 | 7.8038 | 0.044509 | 67.7449 | 71.116 | 25 | 11.2393 | 65.5974 | 67.406 | 25 | 9.8551 | 65.1032 | 9.599 | 180000.0417 | 46.116 | 0.3187 | 0.52051 | 180000 | 0 | 0 | 0.041667 | 67.7525 | 0.044853 | 0.013 | 178284.4167 | 0.3145 | 0.53061 | 1715.625 | 0.75487 | 46.116 | 68.082 | 3.7336 | 0 | [7 empty] | 180000 | 42.406 | 0.070171 | 0.11391 | 179999.9583 | 0 | 0 | 0.041667 | 65.5979 | 0.037836 | 0.012 | 179169.9583 | 0.069344 | 0.11572 | 830.0417 | 0.24867 | 42.406 | 65.7842 | 6.1213 | 0 | [7 empty] | 43200 | 7852905.2212 | inf | 7852905.2212 | 7852905.2212 | 2.9536e+31 | 3926452.6106 | 46.116 | 48.058 | 6719049.5426 | inf | 6719049.5426 | 6719049.5426 | 2.7861e+41 | 3359524.7713 | 42.406 | 46.203 | Diode | 10757.4044 | 9204.1775
Image_H100_ImageSize_32 | H_100 | 3600 | 0.44828 | 0.86506 | 0.25337 | 0.44828 | 1.9298 | 0.58625 | 33.7089 | 16.0714 | 464 | 1.1514 | 0.81992 | 0.25577 | 0.56415 | 28.2077 | 0.86183 | 5.208 | 5.52 | 10.2948 | 11.213 | 231 | 15.5036 | 0.14852 | 232 | 24 | 0 | 0.60884 | 8.1173e-08 | 0.58469 | 0.40688 | 0.014932 | 0.16933 | 0.576 | 0.61062 | 0.61066 | 0.58385 | 0.039496 | 0 | 0.14094 | 76.0438 | 23.3736 | 0.37502 | 0.053716 | 0.012963 | 0.16758 | 0.0083248 | 0.51483 | 0.48853 | 0.46708 | 0.45534 | 0.51028 | 0.29333 | 0.30424 | 0.068075 | 0.037355 | 0.038272 | 0.0053346 | 0.0031312 | 0.0031314 | 0.60083 | 2.1948 | 0.45759 | 0.31942 | 0.86006 | 0.18525 | 0.39076 | 0.8852 | 0.19665 | 0.60856 | 3.368 | 0.37368 | 0.51323 | 2.4219 | 0.27197 | 0.57681 | 2.7095 | 0.30995 | 0.60222 | 16.4177 | 0.31328 | 0.58454 | 15.7244 | 0.30088 | 0.58338 | 15.927 | 0.30321 | 444 | 0.12854 | 0.037902 | 0.019296 | 0.55369 | 0.0012562 | 0.55703 | 0.10309 | 0.082359 | 0.2465 | 0.44828 | 1 | 237.0244 | 844.7903 | 70.2707 | 196.1497 | 186.7893 | 369.0614 | 255.0061 | 15.7291 | 30.835 | 21.1708 | 50.7192 | 7.7668 | 0.045177 | 78.4264 | 83.6663 | 25 | 15.0466 | 75.7382 | 78.2213 | 25 | 12.5157 | 75.1234 | 12.0646 | 180000.0417 | 58.6663 | 0.3991 | 0.76513 | 179971.0417 | 28.9583 | 0 | 0.041667 | 78.4363 | 0.055983 | 0.013 | 179068.4167 | 0.39241 | 0.78871 | 931.625 | 1.6854 | 58.6663 | 79.6042 | 9.0236 | 28.9583 | 5.0416 | 5.0301 | 5.1075 | 5.1075 | 5.0429 | 80.9657 | 130.6667 | 180000 | 53.2213 | 0.08733 | 0.16584 | 179999.9583 | 0 | 0 | 0.041667 | 75.7388 | 0.044723 | 0.012 | 179268.9583 | 0.086177 | 0.17095 | 731.0417 | 0.37009 | 53.2213 | 75.9027 | 8.6636 | 0 | [7 empty] | 43200 | 1925453.7447 | inf | 1925453.7447 | 1925453.7447 | 4.2275e+28 | 962726.8729 | 58.6663 | 54.3332 | 1668505.8208 | inf | 1668505.8208 | 1668505.8208 | 6.7466e+38 | 834252.9104 | 53.2213 | 51.6106 | Diode | 2637.6079 | 2285.6244
Image_H100_ImageSize_64 | H_100 | 3600 | 0.8439 | 1.1874 | 0.25572 | 0.8439 | 1.407 | 0.9144 | 64.3933 | 21.9512 | 351 | 1.6475 | 1.1589 | 0.2651 | 0.89377 | 44.6885 | 1.1845 | 13.2267 | 14.14 | 7.3102 | 8.24 | 175 | 20.5369 | 0.18647 | 179.5 | 175.5 | 0 | 0.92459 | 0.00014327 | 0.9126 | 0.74691 | 0.027606 | 0.87537 | 0.88096 | 0.92104 | 0.92674 | 0.91221 | 0.094024 | 0 | 0.1568 | 89.7647 | 9.6777 | 0.31453 | 0.054986 | 0.031336 | 0.87522 | 0.04295 | 0.93717 | 0.90678 | 0.8609 | 0.86174 | 0.7889 | 0.6099 | 0.63928 | 0.086315 | 0.065208 | 0.067077 | 0.015454 | 0.017198 | 0.017198 | 0.9148 | 4.6521 | 0.96482 | 0.39504 | 1.4263 | 0.31429 | 0.16056 | 0.52788 | 0.11191 | 0.91768 | 9.6073 | 0.98484 | 0.69431 | 5.2189 | 0.58574 | 0.89897 | 5.582 | 0.67705 | 0.91583 | 48.5499 | 0.88539 | 0.90965 | 46.0597 | 0.85224 | 0.90885 | 45.5895 | 0.84897 | 329 | 0.65291 | 0.094024 | 0.043596 | 0.90726 | 0.018365 | 1.2776 | 0.2396 | 0.48035 | 0.44272 | 0.8439 | 1 | 431.4624 | 1159.554 | 127.9158 | 269.2338 | 365.4195 | 520.4743 | 408.9504 | 30.3822 | 43.1021 | 33.6482 | 48.8546 | 7.6761 | 0.046901 | 129.4308 | 136.1729 | 25 | 26.3779 | 124.1564 | 128.3567 | 25 | 23.815 | 122.9689 | 23.4267 | 179996.125 | 111.1729 | 0.78372 | 1.104 | 179820.1667 | 175.9167 | 0 | 0.041667 | 129.4514 | 0.062477 | 0.013 | 172848.5833 | 0.76438 | 1.1447 | 7147.5417 | 1.2514 | 111.1729 | 131.5254 | 1.3388 | 175.9167 | 7.6807 | 7.7471 | 7.8643 | 8.0009 | 7.725 | 128.8197 | 37.3016 | 179996.0833 | 103.3567 | 0.16889 | 0.23655 | 179996.0417 | 0 | 0 | 0.041667 | 124.1576 | 0.046386 | 0.012 | 173141.875 | 0.16524 | 0.24068 | 6854.2083 | 0.26101 | 103.3567 | 126.5727 | 0.96315 | 0 | [7 empty] | 43200 | 57881.1874 | inf | 57881.1874 | 57881.1874 | 1.6389e+25 | 28940.5976 | 111.1729 | 80.5865 | 43727.9094 | inf | 43727.9094 | 43727.9094 | 4.463e+35 | 21863.9547 | 103.3567 | 76.6783 | Diode | 79.2893 | 59.9012
Image_H100_ModelSize_128 | H_100 | 3600 | 0.44828 | 0.86506 | 0.25337 | 0.44828 | 1.9298 | 0.58625 | 33.7089 | 16.0714 | 464 | 1.1514 | 0.81992 | 0.25577 | 0.56415 | 28.2077 | 0.86183 | 5.208 | 5.52 | 10.2948 | 11.213 | 231 | 15.5036 | 0.14852 | 232 | 24 | 0 | 0.60884 | 8.1173e-08 | 0.58469 | 0.40688 | 0.014932 | 0.16933 | 0.576 | 0.61062 | 0.61066 | 0.58385 | 0.039496 | 0 | 0.14094 | 76.0438 | 23.3736 | 0.37502 | 0.053716 | 0.012963 | 0.16758 | 0.0083248 | 0.51483 | 0.48853 | 0.46708 | 0.45534 | 0.51028 | 0.29333 | 0.30424 | 0.068075 | 0.037355 | 0.038272 | 0.0053346 | 0.0031312 | 0.0031314 | 0.60083 | 2.1948 | 0.45759 | 0.31942 | 0.86006 | 0.18525 | 0.39076 | 0.8852 | 0.19665 | 0.60856 | 3.368 | 0.37368 | 0.51323 | 2.4219 | 0.27197 | 0.57681 | 2.7095 | 0.30995 | 0.60222 | 16.4177 | 0.31328 | 0.58454 | 15.7244 | 0.30088 | 0.58338 | 15.927 | 0.30321 | 444 | 0.12854 | 0.037902 | 0.019296 | 0.55369 | 0.0012562 | 0.55703 | 0.10309 | 0.082359 | 0.2465 | 0.44828 | 1 | 237.0244 | 844.7903 | 70.2707 | 196.1497 | 186.7893 | 369.0614 | 255.0061 | 15.7291 | 30.835 | 21.1708 | 50.7192 | 7.7668 | 0.045177 | 78.4264 | 83.6663 | 25 | 15.0466 | 75.7382 | 78.2213 | 25 | 12.5157 | 75.1234 | 12.0646 | 180000.0417 | 58.6663 | 0.3991 | 0.76513 | 179971.0417 | 28.9583 | 0 | 0.041667 | 78.4363 | 0.055983 | 0.013 | 179068.4167 | 0.39241 | 0.78871 | 931.625 | 1.6854 | 58.6663 | 79.6042 | 9.0236 | 28.9583 | 5.0416 | 5.0301 | 5.1075 | 5.1075 | 5.0429 | 80.9657 | 130.6667 | 180000 | 53.2213 | 0.08733 | 0.16584 | 179999.9583 | 0 | 0 | 0.041667 | 75.7388 | 0.044723 | 0.012 | 179268.9583 | 0.086177 | 0.17095 | 731.0417 | 0.37009 | 53.2213 | 75.9027 | 8.6636 | 0 | [7 empty] | 43200 | 1925453.7447 | inf | 1925453.7447 | 1925453.7447 | 4.2275e+28 | 962726.8729 | 58.6663 | 54.3332 | 1668505.8208 | inf | 1668505.8208 | 1668505.8208 | 6.7466e+38 | 834252.9104 | 53.2213 | 51.6106 | Diode | 2637.6079 | 2285.6244
Image_H100_ModelSize_256 | H_100 | 3600 | 0.5448 | 1.1469 | 0.25563 | 0.5448 | 2.1051 | 0.87487 | 32.9644 | 28.125 | 255 | 1.5647 | 1.1221 | 0.25944 | 0.86265 | 43.1327 | 1.1422 | 9.2846 | 9.56 | 18.8965 | 20.58 | 127 | 28.1811 | 0.044136 | 127.5 | 127.5 | 0 | 0.8829 | 5.9539e-05 | 0.87371 | 0.78058 | 0.030465 | 0.87271 | 0.87319 | 0.8855 | 0.89021 | 0.87349 | 0.053991 | 0 | 0.066424 | 90.502 | 9.0844 | 0.27694 | 0.047383 | 0.022924 | 0.87022 | -0.016645 | 0.67069 | 0.61916 | 0.57505 | 0.55715 | 0.76021 | 0.57129 | 0.5994 | 0.058159 | 0.041165 | 0.042551 | 0.0010759 | 0.00028063 | 0.00028063 | 0.87815 | 4.2644 | 0.88587 | 0.27929 | 0.95004 | 0.21013 | 0.024484 | 0.09886 | 0.019772 | 0.8788 | 8.9559 | 0.91924 | 0.54996 | 3.7979 | 0.4249 | 0.83247 | 3.9365 | 0.49159 | 0.87833 | 30.6137 | 0.62119 | 0.87475 | 28.5948 | 0.58644 | 0.87414 | 27.8259 | 0.57366 | 255 | 0.6494 | 0.053991 | 0.02102 | 0.86959 | 0.007305 | 0.68028 | 0.26681 | 0.46815 | 0.40983 | 0.5448 | 1 | 308.7807 | 1120.0008 | 91.5443 | 260.0501 | 231.6484 | 501.0331 | 389.8975 | 19.3756 | 41.5374 | 32.1167 | 49.7294 | 7.7186 | 0.046076 | 91.2229 | 98.7009 | 25 | 19.7471 | 87.8839 | 91.1643 | 25 | 15.6473 | 87.1266 | 14.9837 | 179996.125 | 73.7009 | 0.49595 | 1.0583 | 179868.1667 | 127.9167 | 0 | 0.041667 | 91.2355 | 0.049211 | 0.013 | 178464 | 0.4867 | 1.0955 | 1532.125 | 1.574 | 73.7009 | 94.9284 | 4.657 | 127.9167 | 7.6368 | 7.6573 | 7.7502 | 7.8111 | 7.6453 | 92.6209 | 39.7508 | 180000 | 66.1643 | 0.10764 | 0.22701 | 179999.9583 | 0 | 0 | 0.041667 | 87.8847 | 0.041143 | 0.012 | 179614.9583 | 0.10654 | 0.23153 | 385.0417 | 0.62392 | 66.1643 | 87.9493 | 14.5919 | 0 | [7 empty] | 43200 | 557024.6093 | inf | 557024.6093 | 557024.6093 | 1.0569e+26 | 278512.4071 | 73.7009 | 61.8505 | 498401.2527 | inf | 498401.2527 | 498401.2527 | 2.922e+36 | 249200.6264 | 66.1643 | 58.0822 | Diode | 763.0474 | 682.7414
Image_H100_ModelSize_512 | H_100 | 3600 | 0.55789 | 1.349 | 0.25497 | 0.55789 | 2.418 | 1.0543 | 28.5533 | 81.8182 | 88 | 1.0896 | 1.2993 | 0.25869 | 1.0406 | 52.0296 | 1.3212 | 23.3395 | 25.594 | 58.4218 | 61.84 | 43 | 81.535 | 0.029494 | 48 | 44 | 44 | 1.0601 | 0.00055529 | 1.0508 | 1.0441 | 0.098107 | 0.16602 | 0.9855 | 1.0578 | 1.0938 | 1.0505 | 0.37834 | 0 | 62.8663 | 32.8057 | 4.2261 | 0.080502 | 0.012778 | 0.00858 | 0.011512 | -0.068003 | 0.72515 | 0.70994 | 0.65314 | 0.59161 | 0.87473 | 0.75514 | 0.79558 | 0.030792 | 0.02575 | 0.026538 | 0.00033882 | 8.883e-05 | 8.883e-05 | 1.0504 | 5.6937 | 1.1768 | 0.12818 | 0.46689 | 0.10594 | 0.0019482 | 0.0025637 | 0.00051273 | 1.0521 | 11.2906 | 1.206 | 0.24767 | 1.994 | 0.22639 | 0.0053648 | 0.014165 | 0.0014165 | 1.0576 | 42.0778 | 0.87682 | 0.98753 | 34.1523 | 0.72526 | 1.0547 | 40.4271 | 0.8536 | 88 | 0.12345 | 0.3744 | 0.19812 | 1.0489 | 0.036425 | 0.74882 | 0.13263 | 0.1022 | 0.24709 | 0.55789 | 1 | 333.8535 | 1317.3611 | 98.9776 | 305.8747 | 239.5844 | 599.226 | 476.6221 | 19.9739 | 49.4113 | 39.082 | 49.2501 | 7.6953 | 0.046525 | 93.4798 | 103.0349 | 25 | 21.8901 | 90.0238 | 94.1715 | 25 | 16.6126 | 89.2431 | 15.9417 | 180000.0417 | 78.0349 | 0.51342 | 1.2422 | 179956 | 3.125 | 40.875 | 0.041667 | 93.4931 | 0.042846 | 0.013 | 177944.4167 | 0.5023 | 1.2556 | 2055.625 | 1.4753 | 78.0349 | 98.7006 | 3.0521 | 44 | 10.2679 | 10.3348 | 10.5474 | 10.5474 | 10.3087 | 95.495 | 89.6368 | 180000 | 69.1715 | 0.111 | 0.26511 | 179999.9583 | 0 | 0 | 0.041667 | 90.0246 | 0.042333 | 0.012 | 179358.4583 | 0.10985 | 0.27318 | 641.5417 | 0.43141 | 69.1715 | 92.0379 | 9.1672 | 0 | [7 empty] | 43200 | 409363.9679 | inf | 409363.9679 | 409363.9679 | 8.7202e+24 | 204685.2125 | 78.0349 | 64.0175 | 391978.6521 | inf | 391978.6521 | 391978.6521 | 2.6034e+35 | 195989.326 | 69.1715 | 59.5857 | Diode | 560.7726 | 536.9571
Text_H100_BatchSize2 | H_100 | 3600 | 0.55738 | 0.65601 | 0.25271 | 0.55738 | 1.177 | 0.36095 | 88.9067 | 45 | 176 | 0.46491 | 0.59233 | 0.25998 | 0.33235 | 16.6176 | 0.64906 | 36.5216 | 43.42 | 4.2636 | 4.82 | 87 | 40.6368 | 0.30187 | 84 | 0 | 0 | 0.39329 | 9.0691e-12 | 0.35188 | 0.21361 | 0.068828 | 0.050787 | 0.32426 | 0.39155 | 0.39598 | 0.34679 | 0.24094 | 0 | 44.0966 | 33.5729 | 21.1307 | 0.99992 | 0.13405 | 0.065896 | 0.011709 | 0.017193 | 0.56561 | 0.58531 | 0.57809 | 0.57904 | 0.28648 | 0.12758 | 0.12985 | 0.034862 | 0.018242 | 0.018312 | 0.022304 | 0.013099 | 0.0131 | 0.36643 | 0.98393 | 0.20141 | 0.097972 | 0.25564 | 0.052003 | 0.050693 | 0.14844 | 0.029695 | 0.3663 | 1.9266 | 0.19672 | 0.13545 | 0.71722 | 0.072958 | 0.058748 | 0.34655 | 0.034669 | 0.34772 | 10.3388 | 0.17422 | 0.22248 | 7.3051 | 0.12327 | 0.18222 | 6.3515 | 0.10649 | 0 | 0.041512 | 0.2302 | 0.082131 | 0.23371 | 0.054527 | 0.33566 | 0.098021 | 0.04294 | 0.11115 | 0.55738 | 1 | 260.401 | 640.6399 | 77.2012 | 148.7485 | 231.9003 | 274.8928 | 154.2087 | 19.5377 | 23.1046 | 12.8781 | 50.7938 | 7.7704 | 0.045111 | 91.3422 | 94.9626 | 25 | 15.4104 | 88.0051 | 90.9217 | 25 | 15.0095 | 87.2414 | 14.9705 | 180000.0417 | 69.9626 | 0.49541 | 0.55377 | 180000 | 0 | 0 | 0.041667 | 91.3544 | 0.044146 | 0.013 | 176937.2917 | 0.492 | 0.59402 | 3062.75 | 0.69249 | 69.9626 | 91.5153 | 1.9837 | 0 | [7 empty] | 180000 | 65.9217 | 0.10847 | 0.1211 | 179999.9583 | 0 | 0 | 0.041667 | 88.0058 | 0.037922 | 0.012 | 176910.5 | 0.10782 | 0.13009 | 3089.5 | 0.1459 | 65.9217 | 88.3515 | 1.5878 | 0 | [7 empty] | 43200 | 737324.4645 | inf | 737324.4645 | 737324.4645 | 3.0596e+30 | 368662.2322 | 69.9626 | 59.9813 | 508418.9958 | inf | 508418.9958 | 508418.9958 | 2.9131e+40 | 254209.4979 | 65.9217 | 57.9608 | Diode | 1010.0335 | 696.4644
Text_H100_BatchSize16 | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414 | 1.2625 | 0.28308 | 0.97944 | 48.972 | 1.3829 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 536 | 268 | 267.5 | 1.1045 | 0.0033464 | 0.99286 | 0.39238 | 0.01274 | 0.17007 | 1.0839 | 1.13 | 1.1336 | 0.96631 | 0.051026 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.11151 | 0.012483 | 1.1458 | 1.1321 | 1.1154 | 1.1105 | 0.93885 | 0.83033 | 0.86975 | 0.21342 | 0.19613 | 0.20093 | 0.085967 | 0.099804 | 0.10017 | 1.098 | 6.3489 | 1.3214 | 0.5986 | 2.9839 | 0.63118 | 0.47019 | 2.8106 | 0.5681 | 1.1093 | 12.5723 | 1.295 | 0.91949 | 9.991 | 1.0414 | 1.0467 | 11.027 | 1.1613 | 1.0736 | 71.9283 | 1.243 | 1.0582 | 70.0547 | 1.2124 | 1.0589 | 70.4741 | 1.2139 | 284 | 0.089418 | 0.051026 | 0.036818 | 0.53716 | 0.0091664 | 1.1001 | 0.28913 | 0.15812 | 0.51407 | 1.1033 | 1 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473 | 163.1904 | 170.6615 | 25 | 32.9138 | 156.2022 | 161.3373 | 25 | 31.1426 | 154.6365 | 30.8462 | 180000.0417 | 145.6615 | 1.0386 | 1.265 | 179732 | 268 | 0 | 0.041667 | 163.2183 | 0.055709 | 0.013 | 177092.2083 | 1.0175 | 1.3318 | 2907.8333 | 2.3244 | 145.6615 | 164.0385 | 2.8338 | 268 | 8.8485 | 8.8654 | 9.1792 | 9.3235 | 8.8756 | 161.273 | 18.7615 | 180000 | 136.3373 | 0.22274 | 0.27032 | 179999.9583 | 0 | 0 | 0.041667 | 156.2038 | 0.052299 | 0.012 | 177105.6667 | 0.21892 | 0.28408 | 2894.3333 | 0.45679 | 136.3373 | 156.3347 | 2.6203 | 0 | [7 empty] | 43200 | 11889.3523 | inf | 11889.3523 | 11889.3523 | 1.1861e+24 | 5944.6809 | 145.6615 | 97.8307 | 8826.4647 | inf | 8826.4647 | 8826.4647 | 4.007e+34 | 4413.2324 | 136.3373 | 93.1687 | Diode | 16.2868 | 12.091
Text_H100_BatchSize32 | H_100 | 3600 | 1.1534 | 1.4317 | 0.26503 | 1.1534 | 1.2413 | 1.0996 | 87.36 | 14.2857 | 503 | 2.5218 | 1.2966 | 0.28786 | 1.0087 | 50.4356 | 1.415 | 12.5153 | 12.84 | 1.7927 | 1.96 | 251 | 14.308 | 0.045065 | 516 | 251.5 | 251.5 | 1.1306 | 0.006143 | 1.0055 | 0.37541 | 0.010074 | 0.72363 | 1.1236 | 1.1646 | 1.1667 | 0.9652 | 0.036478 | 0 | 0.062454 | 35.0869 | 62.2372 | 1.967 | 0.54333 | 0.10309 | 0.61738 | -0.011063 | 1.193 | 1.1783 | 1.1637 | 1.1595 | 0.99259 | 0.86874 | 0.91612 | 0.22136 | 0.21537 | 0.22045 | 0.10294 | 0.12555 | 0.12559 | 1.1342 | 6.4419 | 1.3335 | 0.60785 | 3.2149 | 0.67751 | 0.43526 | 2.7149 | 0.54634 | 1.1219 | 13.2901 | 1.3669 | 0.9065 | 10.2546 | 1.0661 | 1.0825 | 11.7933 | 1.2367 | 1.1072 | 77.6101 | 1.3356 | 1.0939 | 75.6983 | 1.305 | 1.0939 | 75.5395 | 1.3033 | 284 | 0.45683 | 0.027611 | 0.014914 | 0.49199 | 0.0017868 | 1.2555 | 0.25804 | 0.34228 | 0.55623 | 1.1534 | 1 | 549.2604 | 1398.1791 | 162.8394 | 324.6396 | 507.5329 | 640.2919 | 500.3092 | 41.978 | 52.6836 | 40.9403 | 48.0943 | 7.6392 | 0.047643 | 169.9807 | 177.5836 | 25 | 34.4764 | 162.6464 | 167.9622 | 25 | 32.7285 | 161.0057 | 32.4237 | 180000.0417 | 152.5836 | 1.0901 | 1.3084 | 179748.0833 | 251.9167 | 0 | 0.041667 | 170.0102 | 0.057843 | 0.013 | 177446.75 | 1.0691 | 1.3656 | 2553.2917 | 2.551 | 152.5836 | 170.8009 | 3.3526 | 251.9167 | 9.2376 | 9.2419 | 9.5055 | 9.6029 | 9.2557 | 167.9175 | 20.2376 | 180000 | 142.9622 | 0.23346 | 0.27933 | 179999.9583 | 0 | 0 | 0.041667 | 162.6482 | 0.055779 | 0.012 | 177446.7917 | 0.22966 | 0.29124 | 2553.2083 | 0.49733 | 142.9622 | 163.0479 | 3.2109 | 0 | [7 empty] | 43200 | 8982.5808 | inf | 8982.5808 | 8982.5808 | 5.7142e+23 | 4491.2961 | 152.5836 | 101.2918 | 6650.9599 | inf | 6650.9599 | 6650.9599 | 2.103e+34 | 3325.48 | 142.9622 | 96.4811 | Diode | 12.3049 | 9.1109
Text_H100_Deepspeedds_z1 | H_100 | 3600 | 1.0289 | 1.4743 | 0.25423 | 1.0289 | 1.433 | 1.1809 | 73.1756 | 13.0435 | 1104 | 2.8028 | 1.2893 | 0.28568 | 1.0036 | 50.1806 | 1.4626 | 4.7976 | 8.81 | 1.7197 | 2.96 | 551 | 6.5102 | 0.43421 | 1348.5 | 296 | 276 | 1.1852 | 0.018295 | 1.1443 | 0.48911 | 0.027587 | 0.31489 | 1.1849 | 1.2102 | 1.2102 | 1.1351 | 0.072364 | 0 | 0.15517 | 45.5815 | 51.7663 | 1.9907 | 0.44603 | 0.060206 | 0.27463 | -0.012042 | 1.1012 | 1.0756 | 1.0467 | 1.0474 | 1.0758 | 1.0012 | 1.0582 | 0.39678 | 0.40523 | 0.41427 | 0.36804 | 0.40461 | 0.40769 | 1.188 | 6.7237 | 1.4069 | 0.87622 | 4.2619 | 0.91509 | 0.95306 | 4.432 | 0.94571 | 1.1883 | 13.5635 | 1.41 | 1.1044 | 11.2576 | 1.2069 | 1.1791 | 11.4444 | 1.2428 | 1.1842 | 75.4798 | 1.3334 | 1.1809 | 72.8954 | 1.3002 | 1.1808 | 72.9234 | 1.3006 | 164 | 0.20176 | 0.045084 | 0.0306 | 0.6815 | 0.017051 | 1.2069 | 0.4699 | 0.19153 | 0.59769 | 1.0289 | 1 | 506.9762 | 1439.7841 | 150.3034 | 334.2997 | 450.658 | 661.6265 | 540.0433 | 37.3292 | 54.379 | 44.1207 | 48.3099 | 7.6496 | 0.04743 | 153.7551 | 162.2481 | 25 | 32.1059 | 147.2449 | 152.4817 | 25 | 29.1761 | 145.7858 | 28.7108 | 180000.0417 | 137.2481 | 0.96756 | 1.38 | 179415.5833 | 580.9583 | 3.4583 | 0.041667 | 153.7811 | 0.045559 | 0.013 | 178619.75 | 0.93199 | 1.3981 | 1380.2917 | 5.5709 | 137.2481 | 154.4545 | 4.678 | 584.4167 | 7.554 | 6.3309 | 9.89 | 10.4713 | 9.3537 | 153.4188 | 6.5904 | 180000 | 127.4817 | 0.20758 | 0.29388 | 179999.9583 | 0 | 0 | 0.041667 | 147.2464 | 0.045173 | 0.012 | 178619.2917 | 0.20118 | 0.29783 | 1380.7083 | 1.0356 | 127.4817 | 147.3304 | 4.6115 | 0 | [7 empty] | 43200 | 16968.2086 | inf | 16968.2086 | 16968.2086 | 4.459e+23 | 8484.1495 | 137.2481 | 93.624 | 13116.9403 | inf | 13116.9403 | 13116.9403 | 1.8869e+34 | 6558.4702 | 127.4817 | 88.7409 | Diode | 23.2441 | 17.9684
Text_H100_Deepspeedds_z2 | H_100 | 3600 | 1.0739 | 1.3964 | 0.25979 | 1.0739 | 1.3003 | 1.0442 | 84.7 | 13.4328 | 559 | 2.1255 | 1.2388 | 0.28116 | 0.95762 | 47.8808 | 1.3718 | 10.9229 | 11.56 | 1.9639 | 2.14 | 279 | 12.8576 | 0.14207 | 559.5 | 279.5 | 260 | 1.102 | 0.0027368 | 0.98334 | 0.39751 | 0.016255 | 0.98353 | 1.0746 | 1.1284 | 1.1285 | 0.97557 | 0.055001 | 0 | 0.3005 | 45.118 | 51.8542 | 2.128 | 0.42275 | 0.17648 | 0.9523 | -0.011038 | 1.1178 | 1.1042 | 1.0874 | 1.084 | 0.96489 | 0.81023 | 0.86307 | 0.22437 | 0.20504 | 0.20995 | 0.098816 | 0.11192 | 0.11212 | 1.0869 | 6.0524 | 1.2566 | 0.60237 | 2.9276 | 0.61984 | 0.53191 | 3.0929 | 0.62597 | 1.0904 | 12.1981 | 1.2632 | 0.93465 | 9.9263 | 1.0353 | 1.0248 | 10.5911 | 1.11 | 1.0571 | 69.2645 | 1.1962 | 1.0437 | 67.2468 | 1.1665 | 1.0434 | 67.1018 | 1.1698 | 289 | 0.70629 | 0.036912 | 0.028889 | 0.54644 | 0.004097 | 1.2657 | 0.29925 | 0.52408 | 0.58555 | 1.0739 | 1 | 514.6392 | 1363.7084 | 152.5752 | 316.6359 | 469.8086 | 622.7155 | 472.7041 | 38.9313 | 51.2845 | 38.7437 | 48.3688 | 7.6525 | 0.047372 | 159.2257 | 166.7905 | 25 | 32.0421 | 152.4395 | 157.5257 | 25 | 30.2712 | 150.9178 | 29.9388 | 180000.0417 | 141.7905 | 1.0086 | 1.2457 | 179720.0417 | 279.9583 | 0 | 0.041667 | 159.2528 | 0.053576 | 0.013 | 176884.7917 | 0.9861 | 1.3497 | 3115.25 | 2.284 | 141.7905 | 160.1633 | 2.5224 | 279.9583 | 8.6847 | 8.7287 | 9.0553 | 9.4164 | 8.7518 | 157.4746 | 16.6207 | 180000 | 132.5257 | 0.21648 | 0.26643 | 179999.9583 | 0 | 0 | 0.041667 | 152.441 | 0.043633 | 0.012 | 176883.4167 | 0.21239 | 0.28272 | 3116.5833 | 0.44817 | 132.5257 | 152.6231 | 1.935 | 0 | [7 empty] | 43200 | 13973.6674 | inf | 13973.6674 | 13973.6674 | 1.7788e+24 | 6986.8388 | 141.7905 | 95.8952 | 10440.0333 | inf | 10440.0333 | 10440.0333 | 5.8193e+34 | 5220.0166 | 132.5257 | 91.2628 | Diode | 19.142 | 14.3014
Text_H100_Deepspeedds_z3 | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414 | 1.2625 | 0.28308 | 0.97944 | 48.972 | 1.3829 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 536 | 268 | 267.5 | 1.1045 | 0.0033464 | 0.99286 | 0.39238 | 0.01274 | 0.17007 | 1.0839 | 1.13 | 1.1336 | 0.96631 | 0.051026 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.11151 | 0.012483 | 1.1458 | 1.1321 | 1.1154 | 1.1105 | 0.93885 | 0.83033 | 0.86975 | 0.21342 | 0.19613 | 0.20093 | 0.085967 | 0.099804 | 0.10017 | 1.098 | 6.3489 | 1.3214 | 0.5986 | 2.9839 | 0.63118 | 0.47019 | 2.8106 | 0.5681 | 1.1093 | 12.5723 | 1.295 | 0.91949 | 9.991 | 1.0414 | 1.0467 | 11.027 | 1.1613 | 1.0736 | 71.9283 | 1.243 | 1.0582 | 70.0547 | 1.2124 | 1.0589 | 70.4741 | 1.2139 | 284 | 0.089418 | 0.051026 | 0.036818 | 0.53716 | 0.0091664 | 1.1001 | 0.28913 | 0.15812 | 0.51407 | 1.1033 | 1 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473 | 163.1904 | 170.6615 | 25 | 32.9138 | 156.2022 | 161.3373 | 25 | 31.1426 | 154.6365 | 30.8462 | 180000.0417 | 145.6615 | 1.0386 | 1.265 | 179732 | 268 | 0 | 0.041667 | 163.2183 | 0.055709 | 0.013 | 177092.2083 | 1.0175 | 1.3318 | 2907.8333 | 2.3244 | 145.6615 | 164.0385 | 2.8338 | 268 | 8.8485 | 8.8654 | 9.1792 | 9.3235 | 8.8756 | 161.273 | 18.7615 | 180000 | 136.3373 | 0.22274 | 0.27032 | 179999.9583 | 0 | 0 | 0.041667 | 156.2038 | 0.052299 | 0.012 | 177105.6667 | 0.21892 | 0.28408 | 2894.3333 | 0.45679 | 136.3373 | 156.3347 | 2.6203 | 0 | [7 empty] | 43200 | 11889.3523 | inf | 11889.3523 | 11889.3523 | 1.1861e+24 | 5944.6809 | 145.6615 | 97.8307 | 8826.4647 | inf | 8826.4647 | 8826.4647 | 4.007e+34 | 4413.2324 | 136.3373 | 93.1687 | Diode | 16.2868 | 12.091
Text_H100_Lamma_1B | H_100 | 3600 | 0.69104 | 1.1725 | 0.25212 | 0.69104 | 1.6967 | 0.86267 | 50.7711 | 4.9451 | 1423 | 2.0909 | 1.08 | 0.2935 | 0.78649 | 39.3245 | 1.1536 | 2.5587 | 2.65 | 2.4997 | 2.58 | 711 | 5.0585 | 0.19477 | 712 | 711.5 | 0 | 0.88674 | 0.00017696 | 0.84092 | 0.22084 | 0.032148 | 0.47909 | 0.87544 | 0.91343 | 0.91444 | 0.84638 | 0.095069 | 0 | 1.1207 | 1.447 | 95.5842 | 0.887 | 0.89019 | 0.0709 | 0.47909 | 0.0067453 | 0.76554 | 0.71654 | 0.70894 | 0.70522 | 0.78025 | 0.57308 | 0.6065 | 0.30221 | 0.20903 | 0.21513 | 0.29701 | 0.19458 | 0.19948 | 0.89743 | 3.1997 | 0.70648 | 0.84677 | 2.9474 | 0.65146 | 0.8579 | 2.995 | 0.66296 | 0.88748 | 6.402 | 0.70435 | 0.85041 | 5.9188 | 0.65418 | 0.86011 | 6.0104 | 0.66477 | 0.86836 | 36.622 | 0.67428 | 0.86249 | 35.762 | 0.6601 | 0.86199 | 36.1263 | 0.66417 | 5 | 0.35874 | 0.082535 | 0.029563 | 0.22136 | 0.02233 | 1.0156 | 0.26116 | 0.29423 | 0.47279 | 0.69104 | 1 | 352.4445 | 1145.0086 | 104.4893 | 265.8566 | 294.3917 | 513.3111 | 384.1786 | 24.6081 | 42.526 | 31.653 | 49.6369 | 7.7141 | 0.046162 | 109.1621 | 116.1092 | 25 | 22.2529 | 104.9181 | 108.6725 | 25 | 19.2397 | 103.9562 | 18.7836 | 180000.0417 | 91.1092 | 0.63038 | 1.0422 | 179288.0833 | 711.9167 | 0 | 0.041667 | 109.1783 | 0.038967 | 0.013 | 178779.8333 | 0.60382 | 1.0983 | 1220.2083 | 4.5207 | 91.1092 | 110.5192 | 4.3402 | 711.9167 | 6.9813 | 6.9811 | 7.187 | 7.7804 | 7.0042 | 109.4008 | 4.8081 | 180000 | 83.6725 | 0.13672 | 0.22432 | 179999.9583 | 0 | 0 | 0.041667 | 104.9191 | 0.038287 | 0.012 | 178743.0417 | 0.13188 | 0.23418 | 1256.9583 | 0.82483 | 83.6725 | 105.4084 | 4.0858 | 0 | [7 empty] | 43200 | 176263.479 | inf | 176263.479 | 176263.479 | 1.2597e+26 | 88131.7543 | 91.1092 | 70.5546 | 140318.7417 | inf | 140318.7417 | 140318.7417 | 3.1951e+36 | 70159.3708 | 83.6725 | 66.8363 | Diode | 241.4568 | 192.2175
Text_H100_Lamma_3B | H_100 | 3600 | 0.91685 | 1.3174 | 0.25419 | 0.91685 | 1.4368 | 0.99294 | 72.2444 | 8.2569 | 856 | 2.2317 | 1.2073 | 0.2662 | 0.94111 | 47.0557 | 1.2951 | 6.0707 | 6.26 | 2.345 | 2.36 | 427 | 8.4043 | 0.20018 | 428 | 428 | 96 | 1.0366 | 0.0016038 | 0.97785 | 0.36748 | 0.061858 | 0.34175 | 1.0005 | 1.0533 | 1.0534 | 0.98058 | 0.21494 | 0 | 3.4802 | 3.5882 | 90.8855 | 1.6989 | 0.29457 | 0.052616 | 0.34042 | 0.00078832 | 0.98781 | 0.96062 | 0.94011 | 0.94088 | 0.87262 | 0.72366 | 0.75255 | 0.22557 | 0.17788 | 0.18321 | 0.10328 | 0.090036 | 0.0903 | 1.0306 | 5.5189 | 1.1449 | 0.82641 | 3.6828 | 0.79131 | 0.96743 | 3.7882 | 0.83914 | 1.0212 | 10.1107 | 1.0738 | 0.97634 | 9.0325 | 0.96744 | 0.98891 | 9.3073 | 0.98795 | 1.0015 | 56.7521 | 1.0064 | 0.99234 | 54.5921 | 0.97961 | 0.99447 | 55.2556 | 0.98694 | 433 | 0.25398 | 0.18446 | 0.066887 | 0.59685 | 0.044455 | 1.1874 | 0.27896 | 0.20935 | 0.48663 | 0.91685 | 1 | 454.7773 | 1286.4983 | 134.828 | 298.7087 | 397.7909 | 583.6751 | 447.2455 | 33.0524 | 48.1691 | 36.7157 | 48.7608 | 7.6716 | 0.046992 | 138.6865 | 146.3645 | 25 | 28.1975 | 132.944 | 137.7472 | 25 | 25.9166 | 131.6521 | 25.5371 | 180000.0417 | 121.3645 | 0.85328 | 1.187 | 179572 | 428 | 0 | 0.041667 | 138.7091 | 0.038949 | 0.013 | 177413.8333 | 0.83105 | 1.2466 | 2586.2083 | 2.3788 | 121.3645 | 140.1737 | 2.0186 | 428 | 8.1952 | 8.1842 | 8.4472 | 9.612 | 8.2482 | 137.7954 | 6.3665 | 180000 | 112.7472 | 0.18374 | 0.25419 | 179999.9583 | 0 | 0 | 0.041667 | 132.9453 | 0.036887 | 0.012 | 177353.0417 | 0.17965 | 0.26808 | 2646.9583 | 0.4575 | 112.7472 | 133.4782 | 1.8141 | 0 | [7 empty] | 43200 | 34946.3342 | inf | 34946.3342 | 34946.3342 | 5.5574e+24 | 17473.1789 | 121.3645 | 85.6823 | 26707.5632 | inf | 26707.5632 | 26707.5632 | 1.7277e+35 | 13353.7816 | 112.7472 | 81.3736 | Diode | 47.8717 | 36.5857
Text_H100_Lamma_8B | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414 | 1.2625 | 0.28308 | 0.97944 | 48.972 | 1.3829 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 536 | 268 | 267.5 | 1.1045 | 0.0033464 | 0.99286 | 0.39238 | 0.01274 | 0.17007 | 1.0839 | 1.13 | 1.1336 | 0.96631 | 0.051026 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.11151 | 0.012483 | 1.1458 | 1.1321 | 1.1154 | 1.1105 | 0.93885 | 0.83033 | 0.86975 | 0.21342 | 0.19613 | 0.20093 | 0.085967 | 0.099804 | 0.10017 | 1.098 | 6.3489 | 1.3214 | 0.5986 | 2.9839 | 0.63118 | 0.47019 | 2.8106 | 0.5681 | 1.1093 | 12.5723 | 1.295 | 0.91949 | 9.991 | 1.0414 | 1.0467 | 11.027 | 1.1613 | 1.0736 | 71.9283 | 1.243 | 1.0582 | 70.0547 | 1.2124 | 1.0589 | 70.4741 | 1.2139 | 284 | 0.089418 | 0.051026 | 0.036818 | 0.53716 | 0.0091664 | 1.1001 | 0.28913 | 0.15812 | 0.51407 | 1.1033 | 1 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473 | 163.1904 | 170.6615 | 25 | 32.9138 | 156.2022 | 161.3373 | 25 | 31.1426 | 154.6365 | 30.8462 | 180000.0417 | 145.6615 | 1.0386 | 1.265 | 179732 | 268 | 0 | 0.041667 | 163.2183 | 0.055709 | 0.013 | 177092.2083 | 1.0175 | 1.3318 | 2907.8333 | 2.3244 | 145.6615 | 164.0385 | 2.8338 | 268 | 8.8485 | 8.8654 | 9.1792 | 9.3235 | 8.8756 | 161.273 | 18.7615 | 180000 | 136.3373 | 0.22274 | 0.27032 | 179999.9583 | 0 | 0 | 0.041667 | 156.2038 | 0.052299 | 0.012 | 177105.6667 | 0.21892 | 0.28408 | 2894.3333 | 0.45679 | 136.3373 | 156.3347 | 2.6203 | 0 | [7 empty] | 43200 | 11889.3523 | inf | 11889.3523 | 11889.3523 | 1.1861e+24 | 5944.6809 | 145.6615 | 97.8307 | 8826.4647 | inf | 8826.4647 | 8826.4647 | 4.007e+34 | 4413.2324 | 136.3373 | 93.1687 | Diode | 16.2868 | 12.091
Text_H100_SeqLength_1024 | H_100 | 3600 | 1.1028 | 1.4045 | 0.25894 | 1.1028 | 1.2736 | 1.0592 | 85.7133 | 6.6667 | 544 | 2.1698 | 1.262 | 0.28835 | 0.97368 | 48.6841 | 1.3842 | 11.3757 | 11.62 | 1.8841 | 2.14 | 271 | 13.2338 | 0.064134 | 544 | 272 | 268 | 1.1104 | 0.0032345 | 0.98584 | 0.38872 | 0.014448 | 0.16622 | 1.0861 | 1.136 | 1.1383 | 0.9556 | 0.045023 | 0 | 0.15489 | 44.8184 | 52.5946 | 1.9177 | 0.42111 | 0.093287 | 0.050748 | -0.01679 | 1.1448 | 1.1369 | 1.1181 | 1.114 | 0.95477 | 0.80745 | 0.86032 | 0.2147 | 0.197 | 0.20193 | 0.086711 | 0.10282 | 0.10289 | 1.0985 | 5.9312 | 1.256 | 0.60175 | 3.0093 | 0.63575 | 0.48973 | 2.8766 | 0.58167 | 1.0996 | 11.9854 | 1.2579 | 0.8941 | 9.6647 | 1.0084 | 1.0439 | 10.9843 | 1.1544 | 1.072 | 71.7941 | 1.2367 | 1.0581 | 70.0069 | 1.2112 | 1.0566 | 69.8519 | 1.2116 | 285 | 0.058418 | 0.038468 | 0.030738 | 0.52758 | 0.0092602 | 1.1013 | 0.28277 | 0.16407 | 0.51177 | 1.1028 | 1 | 527.0567 | 1371.6325 | 156.2567 | 318.4758 | 483.4427 | 626.748 | 480.1819 | 40.0343 | 51.6056 | 39.3389 | 48.2716 | 7.6478 | 0.047468 | 163.1132 | 170.5563 | 25 | 32.8974 | 156.129 | 161.3265 | 25 | 31.2284 | 154.5642 | 30.8987 | 180000.0417 | 145.5563 | 1.038 | 1.2642 | 179728 | 272 | 0 | 0.041667 | 163.1412 | 0.06258 | 0.013 | 177116 | 1.0166 | 1.3363 | 2884.0417 | 2.3515 | 145.5563 | 163.9016 | 3.2852 | 272 | 8.8233 | 8.8293 | 9.1756 | 9.3246 | 8.8573 | 161.1993 | 23.0097 | 180000 | 136.3265 | 0.22262 | 0.27016 | 179999.9583 | 0 | 0 | 0.041667 | 156.1306 | 0.050454 | 0.012 | 177075.0417 | 0.21874 | 0.28511 | 2924.9583 | 0.45784 | 136.3265 | 156.3735 | 2.4812 | 0 | [7 empty] | 43200 | 11941.0933 | inf | 11941.0933 | 11941.0933 | 1.2014e+24 | 5970.5515 | 145.5563 | 97.7781 | 8830.5947 | inf | 8830.5947 | 8830.5947 | 4.0678e+34 | 4415.2973 | 136.3265 | 93.1633 | Diode | 16.3577 | 12.0967
Text_H100_SeqLength_2048 | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414 | 1.2625 | 0.28308 | 0.97944 | 48.972 | 1.3829 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 536 | 268 | 267.5 | 1.1045 | 0.0033464 | 0.99286 | 0.39238 | 0.01274 | 0.17007 | 1.0839 | 1.13 | 1.1336 | 0.96631 | 0.051026 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.11151 | 0.012483 | 1.1458 | 1.1321 | 1.1154 | 1.1105 | 0.93885 | 0.83033 | 0.86975 | 0.21342 | 0.19613 | 0.20093 | 0.085967 | 0.099804 | 0.10017 | 1.098 | 6.3489 | 1.3214 | 0.5986 | 2.9839 | 0.63118 | 0.47019 | 2.8106 | 0.5681 | 1.1093 | 12.5723 | 1.295 | 0.91949 | 9.991 | 1.0414 | 1.0467 | 11.027 | 1.1613 | 1.0736 | 71.9283 | 1.243 | 1.0582 | 70.0547 | 1.2124 | 1.0589 | 70.4741 | 1.2139 | 284 | 0.089418 | 0.051026 | 0.036818 | 0.53716 | 0.0091664 | 1.1001 | 0.28913 | 0.15812 | 0.51407 | 1.1033 | 1 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473 | 163.1904 | 170.6615 | 25 | 32.9138 | 156.2022 | 161.3373 | 25 | 31.1426 | 154.6365 | 30.8462 | 180000.0417 | 145.6615 | 1.0386 | 1.265 | 179732 | 268 | 0 | 0.041667 | 163.2183 | 0.055709 | 0.013 | 177092.2083 | 1.0175 | 1.3318 | 2907.8333 | 2.3244 | 145.6615 | 164.0385 | 2.8338 | 268 | 8.8485 | 8.8654 | 9.1792 | 9.3235 | 8.8756 | 161.273 | 18.7615 | 180000 | 136.3373 | 0.22274 | 0.27032 | 179999.9583 | 0 | 0 | 0.041667 | 156.2038 | 0.052299 | 0.012 | 177105.6667 | 0.21892 | 0.28408 | 2894.3333 | 0.45679 | 136.3373 | 156.3347 | 2.6203 | 0 | [7 empty] | 43200 | 11889.3523 | inf | 11889.3523 | 11889.3523 | 1.1861e+24 | 5944.6809 | 145.6615 | 97.8307 | 8826.4647 | inf | 8826.4647 | 8826.4647 | 4.007e+34 | 4413.2324 | 136.3373 | 93.1687 | Diode | 16.2868 | 12.091
Text_H100_SeqLength_4096 | H_100 | 3600 | 1.1002 | 1.4021 | 0.26093 | 1.1002 | 1.2744 | 1.0597 | 85.56 | 13.4328 | 536 | 2.2411 | 1.2627 | 0.28145 | 0.98121 | 49.0603 | 1.3823 | 11.4909 | 11.72 | 1.9346 | 2.08 | 267 | 13.41 | 0.02735 | 552 | 268 | 267.5 | 1.1122 | 0.0033674 | 0.99385 | 0.39724 | 0.01131 | 0.18958 | 1.0907 | 1.1336 | 1.1339 | 0.96827 | 0.048835 | 0 | 0.052026 | 45.5774 | 51.8231 | 2.0413 | 0.41035 | 0.095876 | 0.032359 | 0.0063762 | 1.1432 | 1.1297 | 1.1105 | 1.1073 | 0.91822 | 0.81736 | 0.85558 | 0.21626 | 0.1994 | 0.20427 | 0.084774 | 0.10161 | 0.10199 | 1.0987 | 6.133 | 1.2951 | 0.58944 | 2.9189 | 0.61795 | 0.4708 | 2.7695 | 0.55689 | 1.1047 | 12.9109 | 1.3277 | 0.89804 | 9.6857 | 1.0114 | 1.0471 | 11.0357 | 1.1581 | 1.0741 | 71.8121 | 1.2413 | 1.0588 | 69.8946 | 1.2103 | 1.0592 | 70.4496 | 1.2145 | 284 | 0.078369 | 0.047343 | 0.034159 | 0.54216 | 0.0075173 | 1.1128 | 0.28835 | 0.16178 | 0.51406 | 1.1002 | 1 | 526.2989 | 1369.2247 | 156.032 | 317.9167 | 482.2831 | 625.5221 | 480.3823 | 39.939 | 51.508 | 39.3557 | 48.2741 | 7.6479 | 0.047465 | 162.7822 | 170.2583 | 25 | 32.8181 | 155.8148 | 160.9118 | 25 | 31.0669 | 154.2537 | 30.7764 | 180000.0417 | 145.2583 | 1.0355 | 1.2644 | 179732 | 268 | 0 | 0.041667 | 162.8101 | 0.058005 | 0.013 | 177109.875 | 1.0142 | 1.3331 | 2890.1667 | 2.3448 | 145.2583 | 163.6373 | 2.9947 | 268 | 8.8474 | 8.8653 | 9.179 | 9.338 | 8.8738 | 160.8854 | 20.2737 | 180000 | 135.9118 | 0.22209 | 0.27022 | 179999.9583 | 0 | 0 | 0.041667 | 155.8164 | 0.054759 | 0.012 | 177084.4167 | 0.21821 | 0.28444 | 2915.5833 | 0.45769 | 135.9118 | 156.0609 | 2.756 | 0 | [7 empty] | 43200 | 12089.0831 | inf | 12089.0831 | 12089.0831 | 1.2099e+24 | 6044.5464 | 145.2583 | 97.6291 | 8991.7534 | inf | 8991.7534 | 8991.7534 | 4.0966e+34 | 4495.8767 | 135.9118 | 92.9559 | Diode | 16.5604 | 12.3175
Image_B200_BatchSize_128 | B_200 | 3600 | 0.65184 | 1.2119 | 0.40032 | 0.65184 | 1.8592 | 0.79231 | 30.1867 | 11.3924 | 632 | 1.5165 | 1.1848 | 0.40683 | 0.77801 | 38.9003 | 1.2087 | 3.422 | 3.48 | 7.9642 | 8.78 | 316 | 11.3863 | 0.05211 | 316 | 316 | 0 | 0.80717 | 2.4154e-05 | 0.78943 | 0.41217 | 0.01155 | 0.11376 | 0.77468 | 0.80821 | 0.81004 | 0.78852 | 0.034987 | 0 | 0.047497 | 73.9386 | 25.4308 | 0.50986 | 0.058211 | 0.014977 | 0.066578 | -0.013138 | 0.72825 | 0.68413 | 0.66325 | 0.65814 | 0.70353 | 0.59361 | 0.6144 | 0.12439 | 0.099498 | 0.10146 | 0.015915 | 0.012465 | 0.012465 | 0.80481 | 3.7643 | 0.79091 | 0.57108 | 2.0831 | 0.45047 | 0.75805 | 2.5085 | 0.56343 | 0.8016 | 5.5168 | 0.61245 | 0.78966 | 5.1485 | 0.574 | 0.79101 | 5.3351 | 0.59449 | 0.79636 | 31.9816 | 0.59563 | 0.79131 | 30.9483 | 0.57618 | 0.79133 | 30.8123 | 0.57406 | 316 | 0.049924 | 0.033398 | 0.018919 | 0.64822 | 0.0032829 | 0.66222 | 0.12879 | 0.074954 | 0.35899 | 0.65184 | 1 | 335.2774 | 1183.4912 | 99.3998 | 274.7918 | 276.8739 | 532.2978 | 359.2093 | 23.1663 | 44.0523 | 29.4277 | 49.7794 | 7.7211 | 0.04603 | 104.1579 | 111.6634 | 25 | 22.08 | 100.1673 | 103.7059 | 25 | 18.4027 | 99.2618 | 17.6995 | 180000.0417 | 86.6634 | 0.59269 | 1.1252 | 179684.0417 | 315.9583 | 0 | 0.041667 | 104.1731 | 0.048354 | 0.013 | 179107.6667 | 0.58133 | 1.1416 | 892.375 | 2.8738 | 86.6634 | 105.0413 | 7.8042 | 315.9583 | 6.8358 | 6.8466 | 6.9442 | 6.9997 | 6.8408 | 105.5222 | 15.8301 | 180000 | 78.7059 | 0.1287 | 0.24116 | 179999.9583 | 0 | 0 | 0.041667 | 100.1682 | 0.043098 | 0.012 | 179219.9583 | 0.12673 | 0.24424 | 780.0417 | 0.58059 | 78.7059 | 100.3419 | 7.6771 | 0 | [7 empty] | 43200 | 231803.9363 | inf | 231803.9363 | 231803.9363 | 3.9218e+25 | 115901.976 | 86.6634 | 68.3317 | 195438.5246 | inf | 195438.5246 | 195438.5246 | 1.2218e+36 | 97719.2623 | 78.7059 | 64.353 | Diode | 317.5396 | 267.724
Image_B200_BatchSize_256 | B_200 | 3600 | 0.64912 | 1.3949 | 0.40261 | 0.64912 | 2.149 | 0.96041 | 23.8711 | 11.1111 | 647 | 1.9164 | 1.3559 | 0.40712 | 0.9488 | 47.44 | 1.3779 | 2.6435 | 2.68 | 8.4886 | 9.28 | 323 | 11.1321 | 0.072785 | 323.5 | 323.5 | 0 | 0.97398 | 0.00073691 | 0.95352 | 0.4306 | 0.01206 | 0.96465 | 0.96469 | 0.99052 | 0.99115 | 0.95359 | 0.044256 | 0 | 0.032596 | 62.7865 | 35.5695 | 1.4669 | 0.10555 | 0.038932 | 0.96358 | 0.019454 | 0.74285 | 0.67741 | 0.66131 | 0.65773 | 0.84547 | 0.7782 | 0.81006 | 0.15442 | 0.13573 | 0.13915 | 0.027811 | 0.015397 | 0.015402 | 0.97224 | 4.516 | 0.97666 | 0.62976 | 2.3875 | 0.52699 | 0.90402 | 2.9189 | 0.65979 | 0.97216 | 6.6065 | 0.75126 | 0.94917 | 6.1743 | 0.70504 | 0.95924 | 6.4291 | 0.7368 | 0.96307 | 38.8512 | 0.73986 | 0.95991 | 37.386 | 0.71285 | 0.96073 | 36.789 | 0.70128 | 321 | 0.71892 | 0.044256 | 0.028758 | 0.63817 | 0.0035978 | 1.1542 | 0.25897 | 0.52473 | 0.54698 | 0.64912 | 1 | 342 | 1362.2452 | 101.3928 | 316.2962 | 276.5825 | 621.9714 | 441.2811 | 23.1181 | 51.2252 | 35.9993 | 49.6284 | 7.7137 | 0.04617 | 104.0692 | 113.0589 | 25 | 23.2855 | 100.0819 | 103.8657 | 25 | 18.5833 | 99.1783 | 17.7142 | 180000.0417 | 88.0589 | 0.59226 | 1.3012 | 179676.0833 | 323.9167 | 0 | 0.041667 | 104.0844 | 0.049375 | 0.013 | 179132.5 | 0.57848 | 1.3203 | 867.5417 | 3.4371 | 88.0589 | 104.2064 | 8.2549 | 323.9167 | 8.2764 | 8.2886 | 8.3586 | 8.4719 | 8.2806 | 106.172 | 16.0183 | 180003.9167 | 78.8657 | 0.12844 | 0.27753 | 180003.875 | 0 | 0 | 0.041667 | 100.0828 | 0.048495 | 0.012 | 179032.7083 | 0.12603 | 0.2813 | 971.2083 | 0.57332 | 78.8657 | 100.3111 | 7.1541 | 0 | [7 empty] | 43200 | 212438.2005 | inf | 212438.2005 | 212438.2005 | 4.5262e+24 | 106219.2837 | 88.0589 | 69.0294 | 193309.7651 | inf | 193309.7651 | 193309.7651 | 1.8915e+35 | 96654.8825 | 78.8657 | 64.4329 | Diode | 291.0112 | 264.8079
Image_B200_BatchSize_512 | B_200 | 3600 | 0.65202 | 1.5094 | 0.40186 | 0.65202 | 2.315 | 1.0803 | 20.5644 | 11.1111 | 656 | 2.2058 | 1.4706 | 0.4073 | 1.0633 | 53.1653 | 1.5038 | 2.2571 | 2.3 | 8.7276 | 9.1 | 328 | 10.9847 | 0.035334 | 328 | 328 | 328 | 1.0962 | 0.0060867 | 1.0623 | 0.42889 | 0.011989 | 0.14876 | 1.0609 | 1.1051 | 1.1051 | 1.0577 | 0.044266 | 0 | 0.018962 | 57.9039 | 40.8257 | 1.1347 | 0.090152 | 0.026503 | 0.0032195 | 0.019106 | 0.75361 | 0.67734 | 0.66247 | 0.65941 | 0.95025 | 0.94492 | 0.98561 | 0.18051 | 0.16936 | 0.17406 | 0.038509 | 0.022855 | 0.022859 | 1.0972 | 5.0355 | 1.1076 | 0.6848 | 2.6333 | 0.58905 | 0.98844 | 3.4458 | 0.79432 | 1.0937 | 7.4013 | 0.85147 | 1.0628 | 6.9492 | 0.80199 | 1.0797 | 7.2352 | 0.83745 | 1.0852 | 43.876 | 0.84469 | 1.08 | 42.25 | 0.81361 | 1.0801 | 42.277 | 0.81108 | 328 | 0.085618 | 0.042927 | 0.031857 | 0.62529 | 0.0059627 | 1.0928 | 0.21384 | 0.08384 | 0.51733 | 0.65202 | 1 | 346.9532 | 1474.0627 | 102.8613 | 342.2588 | 278.3131 | 679.3034 | 501.0699 | 23.2491 | 55.7814 | 40.756 | 49.5424 | 7.7095 | 0.04625 | 104.5599 | 114.6089 | 25 | 24.1752 | 100.5471 | 104.5578 | 25 | 18.8618 | 99.6383 | 17.8366 | 180000.0417 | 89.6089 | 0.59606 | 1.4278 | 179672.0417 | 327.9583 | 0 | 0.041667 | 104.5752 | 0.048292 | 0.013 | 178836.7917 | 0.57996 | 1.457 | 1163.25 | 3.0712 | 89.6089 | 104.5447 | 6.0244 | 327.9583 | 9.358 | 9.3581 | 9.4746 | 9.5398 | 9.3615 | 107.167 | 14.8263 | 180000 | 79.5578 | 0.12918 | 0.30362 | 179999.9583 | 0 | 0 | 0.041667 | 100.5479 | 0.04704 | 0.012 | 178806.5 | 0.12635 | 0.309 | 1193.5 | 0.55349 | 79.5578 | 100.4873 | 5.6321 | 0 | [7 empty] | 43200 | 193081.0952 | inf | 193081.0952 | 193081.0952 | 1.1602e+24 | 96541.772 | 89.6089 | 69.8045 | 184396.8605 | inf | 184396.8605 | 184396.8605 | 5.8416e+34 | 92198.4302 | 79.5578 | 64.7789 | Diode | 264.4947 | 252.5984
Image_B200_ImageSize_32 | B_200 | 3600 | 0.65184 | 1.2119 | 0.40032 | 0.65184 | 1.8592 | 0.79231 | 30.1867 | 11.3924 | 632 | 1.5165 | 1.1848 | 0.40683 | 0.77801 | 38.9003 | 1.2087 | 3.422 | 3.48 | 7.9642 | 8.78 | 316 | 11.3863 | 0.05211 | 316 | 316 | 0 | 0.80717 | 2.4154e-05 | 0.78943 | 0.41217 | 0.01155 | 0.11376 | 0.77468 | 0.80821 | 0.81004 | 0.78852 | 0.034987 | 0 | 0.047497 | 73.9386 | 25.4308 | 0.50986 | 0.058211 | 0.014977 | 0.066578 | -0.013138 | 0.72825 | 0.68413 | 0.66325 | 0.65814 | 0.70353 | 0.59361 | 0.6144 | 0.12439 | 0.099498 | 0.10146 | 0.015915 | 0.012465 | 0.012465 | 0.80481 | 3.7643 | 0.79091 | 0.57108 | 2.0831 | 0.45047 | 0.75805 | 2.5085 | 0.56343 | 0.8016 | 5.5168 | 0.61245 | 0.78966 | 5.1485 | 0.574 | 0.79101 | 5.3351 | 0.59449 | 0.79636 | 31.9816 | 0.59563 | 0.79131 | 30.9483 | 0.57618 | 0.79133 | 30.8123 | 0.57406 | 316 | 0.049924 | 0.033398 | 0.018919 | 0.64822 | 0.0032829 | 0.66222 | 0.12879 | 0.074954 | 0.35899 | 0.65184 | 1 | 335.2774 | 1183.4912 | 99.3998 | 274.7918 | 276.8739 | 532.2978 | 359.2093 | 23.1663 | 44.0523 | 29.4277 | 49.7794 | 7.7211 | 0.04603 | 104.1579 | 111.6634 | 25 | 22.08 | 100.1673 | 103.7059 | 25 | 18.4027 | 99.2618 | 17.6995 | 180000.0417 | 86.6634 | 0.59269 | 1.1252 | 179684.0417 | 315.9583 | 0 | 0.041667 | 104.1731 | 0.048354 | 0.013 | 179107.6667 | 0.58133 | 1.1416 | 892.375 | 2.8738 | 86.6634 | 105.0413 | 7.8042 | 315.9583 | 6.8358 | 6.8466 | 6.9442 | 6.9997 | 6.8408 | 105.5222 | 15.8301 | 180000 | 78.7059 | 0.1287 | 0.24116 | 179999.9583 | 0 | 0 | 0.041667 | 100.1682 | 0.043098 | 0.012 | 179219.9583 | 0.12673 | 0.24424 | 780.0417 | 0.58059 | 78.7059 | 100.3419 | 7.6771 | 0 | [7 empty] | 43200 | 231803.9363 | inf | 231803.9363 | 231803.9363 | 3.9218e+25 | 115901.976 | 86.6634 | 68.3317 | 195438.5246 | inf | 195438.5246 | 195438.5246 | 1.2218e+36 | 97719.2623 | 78.7059 | 64.353 | Diode | 317.5396 | 267.724
Image_B200_ImageSize_64 | B_200 | 3600 | 1.0173 | 1.5695 | 0.4055 | 1.0173 | 1.5429 | 1.126 | 52.9178 | 18.3673 | 392 | 2.073 | 1.5275 | 0.41783 | 1.1097 | 55.4844 | 1.5506 | 9.7012 | 9.78 | 8.6651 | 9.1 | 196 | 18.3664 | 0.023299 | 200 | 196 | 195.5 | 1.1457 | 0.0078083 | 1.125 | 0.89365 | 0.029223 | 0.27258 | 1.0966 | 1.1549 | 1.1573 | 1.1243 | 0.10305 | 0 | 0.023059 | 87.7175 | 11.8978 | 0.31887 | 0.032617 | 0.010097 | 0.27258 | 0.056478 | 1.142 | 1.0812 | 1.0332 | 1.0354 | 0.97495 | 1.006 | 1.0414 | 0.11405 | 0.1126 | 0.1154 | 0.011802 | 0.015664 | 0.015664 | 1.1369 | 7.4624 | 1.5506 | 0.54905 | 2.7083 | 0.58676 | 0.49041 | 1.8934 | 0.39498 | 1.1339 | 15.5383 | 1.6005 | 1.0658 | 10.6426 | 1.1715 | 1.1193 | 10.6916 | 1.2181 | 1.1284 | 72.3116 | 1.3342 | 1.1256 | 68.7027 | 1.285 | 1.1265 | 68.1294 | 1.2756 | 392 | 0.20435 | 0.098864 | 0.05339 | 1.1169 | 0.02662 | 0.81298 | 0.15616 | 0.09285 | 0.42627 | 1.0173 | 1 | 525.7733 | 1532.7628 | 155.8762 | 355.8882 | 449.4157 | 709.7818 | 524.9165 | 37.1237 | 58.1946 | 42.6288 | 47.9091 | 7.6301 | 0.047827 | 153.3771 | 162.8751 | 25 | 33.5339 | 146.8808 | 152.2169 | 25 | 29.4039 | 145.4297 | 28.7241 | 180000.0417 | 137.8751 | 0.96566 | 1.4945 | 179804.0417 | 46.1667 | 149.7917 | 0.041667 | 153.4034 | 0.044335 | 0.013 | 178306.7083 | 0.95283 | 1.5121 | 1693.3333 | 2.3162 | 137.8751 | 156.1296 | 3.5859 | 195.9583 | 10.0307 | 10.0325 | 10.1517 | 10.3747 | 10.0373 | 153.4522 | 19.4442 | 180000 | 127.2169 | 0.20648 | 0.31663 | 179999.9583 | 0 | 0 | 0.041667 | 146.8823 | 0.04291 | 0.012 | 179081.5 | 0.20465 | 0.3203 | 918.5 | 0.56329 | 127.2169 | 147.9603 | 6.3342 | 0 | [7 empty] | 43200 | 16514.4068 | inf | 16514.4068 | 16514.4068 | 5.6821e+22 | 8257.2487 | 137.8751 | 93.9375 | 13277.7293 | inf | 13277.7293 | 13277.7293 | 3.0004e+33 | 6638.8647 | 127.2169 | 88.6084 | Diode | 22.6225 | 18.1887
Image_B200_ImageSize_128 | B_200 | 3600 | 1.3126 | 1.5049 | 0.41562 | 1.3126 | 1.1465 | 1.0564 | 86.0489 | 69.2308 | 112 | 1.4001 | 1.4457 | 0.42703 | 1.0187 | 50.934 | 1.4989 | 54.9415 | 60.06 | 9.5057 | 11.06 | 55 | 63.98 | 0.28196 | 88 | 52 | 52 | 1.0565 | 0.00054399 | 1.0333 | 0.79062 | 0.046609 | 0.15643 | 0.99736 | 1.0749 | 1.0828 | 1.031 | 0.15366 | 0 | 31.9189 | 60.8605 | 6.6043 | 0.24406 | 0.18916 | 0.18309 | 0.010244 | -0.016593 | 1.3508 | 1.4454 | 1.3519 | 1.3283 | 0.90169 | 0.89674 | 0.93419 | 0.089085 | 0.11165 | 0.11222 | 0.071356 | 0.10239 | 0.1024 | 1.0575 | 6.1457 | 1.3053 | 0.19786 | 1.102 | 0.2282 | 0.07302 | 0.52612 | 0.10523 | 1.0617 | 13.8736 | 1.4325 | 0.31141 | 3.3465 | 0.34893 | 0.073544 | 1.0624 | 0.10625 | 1.0619 | 83.7864 | 1.4341 | 0.92677 | 72.0899 | 1.2408 | 1.057 | 81.9588 | 1.4107 | 104 | 0.055063 | 0.15022 | 0.067692 | 0.97598 | 0.029047 | 0.77561 | 0.14659 | 0.076122 | 0.27754 | 1.3126 | 1 | 621.8799 | 1469.6426 | 184.3689 | 341.2325 | 585.0244 | 677.019 | 490.6549 | 48.1884 | 55.6003 | 39.892 | 47.4976 | 7.6101 | 0.048241 | 192.0737 | 200.1238 | 25 | 39.2307 | 183.6118 | 189.9394 | 25 | 37.7968 | 181.7284 | 37.4004 | 180000.0417 | 175.1238 | 1.2581 | 1.4199 | 179948 | 52 | 0 | 0.041667 | 192.1085 | 0.051728 | 0.013 | 174731.4583 | 1.2437 | 1.4376 | 5268.5833 | 1.7348 | 175.1238 | 192.6605 | 1.4367 | 52 | 9.5748 | 9.5859 | 9.9498 | 9.9527 | 9.5946 | 189.6476 | 53.5986 | 180000 | 164.9394 | 0.2681 | 0.30255 | 179999.9583 | 0 | 0 | 0.041667 | 183.6139 | 0.050208 | 0.012 | 174253.4167 | 0.26534 | 0.3062 | 5746.5833 | 0.35164 | 164.9394 | 183.5115 | 1.2612 | 0 | [7 empty] | 43200 | 3854.4936 | inf | 3854.4936 | 3854.4936 | 6.3821e+22 | 1927.2474 | 175.1238 | 112.5619 | 2791.4429 | inf | 2791.4429 | 2791.4429 | 2.7657e+33 | 1395.7215 | 164.9394 | 107.4697 | Diode | 5.2801 | 3.8239
Image_B200_ModelSize_128 | B_200 | 3600 | 0.65184 | 1.2119 | 0.40032 | 0.65184 | 1.8592 | 0.79231 | 30.1867 | 11.3924 | 632 | 1.5165 | 1.1848 | 0.40683 | 0.77801 | 38.9003 | 1.2087 | 3.422 | 3.48 | 7.9642 | 8.78 | 316 | 11.3863 | 0.05211 | 316 | 316 | 0 | 0.80717 | 2.4154e-05 | 0.78943 | 0.41217 | 0.01155 | 0.11376 | 0.77468 | 0.80821 | 0.81004 | 0.78852 | 0.034987 | 0 | 0.047497 | 73.9386 | 25.4308 | 0.50986 | 0.058211 | 0.014977 | 0.066578 | -0.013138 | 0.72825 | 0.68413 | 0.66325 | 0.65814 | 0.70353 | 0.59361 | 0.6144 | 0.12439 | 0.099498 | 0.10146 | 0.015915 | 0.012465 | 0.012465 | 0.80481 | 3.7643 | 0.79091 | 0.57108 | 2.0831 | 0.45047 | 0.75805 | 2.5085 | 0.56343 | 0.8016 | 5.5168 | 0.61245 | 0.78966 | 5.1485 | 0.574 | 0.79101 | 5.3351 | 0.59449 | 0.79636 | 31.9816 | 0.59563 | 0.79131 | 30.9483 | 0.57618 | 0.79133 | 30.8123 | 0.57406 | 316 | 0.049924 | 0.033398 | 0.018919 | 0.64822 | 0.0032829 | 0.66222 | 0.12879 | 0.074954 | 0.35899 | 0.65184 | 1 | 335.2774 | 1183.4912 | 99.3998 | 274.7918 | 276.8739 | 532.2978 | 359.2093 | 23.1663 | 44.0523 | 29.4277 | 49.7794 | 7.7211 | 0.04603 | 104.1579 | 111.6634 | 25 | 22.08 | 100.1673 | 103.7059 | 25 | 18.4027 | 99.2618 | 17.6995 | 180000.0417 | 86.6634 | 0.59269 | 1.1252 | 179684.0417 | 315.9583 | 0 | 0.041667 | 104.1731 | 0.048354 | 0.013 | 179107.6667 | 0.58133 | 1.1416 | 892.375 | 2.8738 | 86.6634 | 105.0413 | 7.8042 | 315.9583 | 6.8358 | 6.8466 | 6.9442 | 6.9997 | 6.8408 | 105.5222 | 15.8301 | 180000 | 78.7059 | 0.1287 | 0.24116 | 179999.9583 | 0 | 0 | 0.041667 | 100.1682 | 0.043098 | 0.012 | 179219.9583 | 0.12673 | 0.24424 | 780.0417 | 0.58059 | 78.7059 | 100.3419 | 7.6771 | 0 | [7 empty] | 43200 | 231803.9363 | inf | 231803.9363 | 231803.9363 | 3.9218e+25 | 115901.976 | 86.6634 | 68.3317 | 195438.5246 | inf | 195438.5246 | 195438.5246 | 1.2218e+36 | 97719.2623 | 78.7059 | 64.353 | Diode | 317.5396 | 267.724
Image_B200_ModelSize_256 | B_200 | 3600 | 0.73378 | 1.5493 | 0.40232 | 0.73378 | 2.1114 | 1.1258 | 27.96 | 21.9512 | 327 | 1.9052 | 1.5219 | 0.40851 | 1.1134 | 55.6676 | 1.5452 | 6.1114 | 6.18 | 15.8861 | 16.66 | 163 | 21.9975 | 0.065551 | 163.5 | 163.5 | 163.5 | 1.1425 | 0.0066566 | 1.1247 | 0.86476 | 0.029706 | 1.1119 | 1.1165 | 1.1408 | 1.1438 | 1.1237 | 0.092291 | 0 | 0.12012 | 89.9932 | 9.417 | 0.39017 | 0.055105 | 0.02448 | 1.1119 | 0.02535 | 0.87065 | 0.80393 | 0.7637 | 0.74497 | 0.98237 | 0.99383 | 1.0378 | 0.094192 | 0.091117 | 0.093371 | 0.0057959 | 0.0067237 | 0.0067237 | 1.1351 | 7.5339 | 1.5655 | 0.46098 | 2.2302 | 0.48194 | 0.14063 | 0.3515 | 0.071029 | 1.1354 | 12.6075 | 1.368 | 0.77243 | 6.6964 | 0.75545 | 1.1087 | 7.8685 | 0.92029 | 1.1312 | 52.0931 | 1.0247 | 1.1255 | 49.5518 | 0.97917 | 1.1249 | 49.9536 | 0.9886 | 324 | 0.82992 | 0.092088 | 0.051966 | 1.1091 | 0.015298 | 0.90121 | 0.34122 | 0.6007 | 0.54113 | 0.73378 | 1 | 400.8373 | 1512.9948 | 118.8363 | 351.2983 | 317.5277 | 699.4885 | 524.1709 | 26.4059 | 57.3802 | 42.585 | 48.8854 | 7.6776 | 0.046872 | 115.738 | 126.1956 | 25 | 27.0192 | 111.1552 | 115.6196 | 25 | 21.3546 | 110.123 | 20.4615 | 180000.0417 | 101.1956 | 0.68095 | 1.4848 | 179836.0833 | 30.7917 | 133.125 | 0.041667 | 115.756 | 0.051685 | 0.013 | 178969.1667 | 0.67098 | 1.5159 | 1030.875 | 2.4122 | 101.1956 | 117.415 | 7.3931 | 163.9167 | 10.0619 | 10.0869 | 10.2081 | 10.3676 | 10.0716 | 117.9524 | 33.5052 | 180003.9167 | 90.6196 | 0.14678 | 0.31459 | 180003.875 | 0 | 0 | 0.041667 | 111.1562 | 0.051824 | 0.012 | 179275.875 | 0.1452 | 0.31939 | 728.0417 | 0.53405 | 90.6196 | 110.9796 | 10.4356 | 0 | [7 empty] | 43200 | 98461.7185 | inf | 98461.7185 | 98461.7185 | 2.4623e+23 | 49231.5929 | 101.1956 | 75.5978 | 90780.1294 | inf | 90780.1294 | 90780.1294 | 1.3759e+34 | 45390.0647 | 90.6196 | 70.3098 | Diode | 134.8791 | 124.3563
Image_B200_ModelSize_512 | B_200 | 3600 | 0.75986 | 1.8138 | 0.40355 | 0.75986 | 2.387 | 1.3778 | 25.1356 | 56.25 | 135 | 1.7137 | 1.7702 | 0.40853 | 1.3616 | 68.0815 | 1.8023 | 13.4976 | 14.16 | 39.9618 | 43.362 | 67 | 53.2579 | 0.11186 | 67.5 | 67.5 | 64.5 | 1.3953 | 0.094901 | 1.373 | 1.3241 | 0.089062 | 1.2247 | 1.3273 | 1.3994 | 1.41 | 1.3724 | 0.13518 | 0 | 7.0407 | 85.9347 | 6.7707 | 0.19301 | 0.03806 | 0.022785 | 1.2247 | -0.0096941 | 0.95381 | 0.87788 | 0.84692 | 0.80324 | 1.1389 | 1.3858 | 1.4444 | 0.055452 | 0.061697 | 0.063258 | 0.00065072 | 0.00026617 | 0.00026617 | 1.3884 | 10.6654 | 2.2206 | 0.22664 | 1.3166 | 0.28367 | 0.0060536 | 0.012393 | 0.0024786 | 1.3895 | 22.3686 | 2.3001 | 0.43285 | 4.5984 | 0.51505 | 0.021629 | 0.10605 | 0.010799 | 1.3801 | 72.1639 | 1.4825 | 1.3777 | 62.8158 | 1.3125 | 1.377 | 60.9371 | 1.2797 | 132 | 0.91214 | 0.10863 | 0.038159 | 1.3693 | 0.049652 | 1.0018 | 0.48877 | 0.73059 | 0.5597 | 0.75986 | 1 | 439.1247 | 1771.2967 | 130.1874 | 411.2728 | 333.349 | 836.3348 | 653.9763 | 27.5984 | 68.1519 | 52.8156 | 48.2371 | 7.6461 | 0.047502 | 120.2227 | 133.46 | 25 | 30.286 | 115.4067 | 120.9244 | 25 | 22.9478 | 114.3279 | 22.0264 | 180000.0417 | 108.46 | 0.7158 | 1.7617 | 179932.0417 | 4 | 63.9583 | 0.041667 | 120.2421 | 0.042085 | 0.013 | 177000.5417 | 0.69492 | 1.8307 | 2999.5 | 1.9478 | 108.46 | 127.1044 | 2.0366 | 67.9583 | 13.0285 | 13.3441 | 13.8176 | 13.9665 | 13.3143 | 123.2649 | 54.618 | 180000 | 95.9244 | 0.15347 | 0.37062 | 179999.9583 | 0 | 0 | 0.041667 | 115.4078 | 0.036186 | 0.012 | 178616.8333 | 0.15101 | 0.38342 | 1383.1667 | 0.47148 | 95.9244 | 117.7973 | 3.4682 | 0 | [7 empty] | 43200 | 66589.227 | inf | 66589.227 | 66589.227 | 1.3652e+22 | 33307.5102 | 108.46 | 79.23 | 66324.2577 | inf | 66324.2577 | 66324.2577 | 8.9872e+32 | 33162.1289 | 95.9244 | 72.9622 | Diode | 91.2181 | 90.8551
Text_B200_BatchSize2 | B_200 | 3600 | 0.78157 | 0.88893 | 0.40656 | 0.78157 | 1.1374 | 0.43512 | 88.8667 | 17.3077 | 208 | 0.6297 | 0.82547 | 0.41558 | 0.40989 | 20.4945 | 0.87259 | 31.2322 | 34 | 3.5638 | 2.7 | 103 | 34.5527 | 0.15805 | 104 | 0 | 0 | 0.47323 | 2.5839e-10 | 0.4221 | 0.20102 | 0.071344 | 0.064825 | 0.40385 | 0.46036 | 0.47365 | 0.41601 | 0.24191 | 0 | 37.3093 | 34.0006 | 27.982 | 0.45967 | 0.20697 | 0.041462 | 0.02236 | 0.0039378 | 0.79035 | 0.81597 | 0.80335 | 0.80346 | 0.35729 | 0.21832 | 0.22225 | 0.038212 | 0.027219 | 0.02732 | 0.019754 | 0.016234 | 0.016235 | 0.44575 | 1.6279 | 0.333 | 0.11071 | 0.39713 | 0.080771 | 0.043958 | 0.18118 | 0.036241 | 0.43981 | 3.444 | 0.3485 | 0.17286 | 1.2943 | 0.13135 | 0.052395 | 0.43052 | 0.043059 | 0.42509 | 16.3595 | 0.27473 | 0.29627 | 13.7409 | 0.23145 | 0.32529 | 15.4476 | 0.25931 | 0 | 0.025059 | 0.22365 | 0.077781 | 0.25383 | 0.052508 | 0.41581 | 0.085996 | 0.052317 | 0.13852 | 0.78157 | 1 | 363.8699 | 868.0945 | 107.8766 | 201.5606 | 331.5703 | 380.0128 | 191.981 | 27.7541 | 31.7287 | 15.865 | 49.8391 | 7.724 | 0.045975 | 119.7982 | 124.522 | 25 | 22.1717 | 115.0197 | 118.9433 | 25 | 21.266 | 113.9349 | 21.2422 | 180000.0417 | 99.522 | 0.7097 | 0.77553 | 179996.4583 | 3.5417 | 0 | 0.041667 | 119.8163 | 0.042189 | 0.013 | 177415.25 | 0.70589 | 0.8093 | 2584.7917 | 0.97088 | 99.522 | 120.1389 | 2.1935 | 3.5417 | 5.1597 | 5.1655 | 5.1655 | 5.1655 | 5.1602 | 121.7805 | 53.993 | 180000 | 93.9433 | 0.15418 | 0.16823 | 179999.9583 | 0 | 0 | 0.041667 | 115.0208 | 0.037052 | 0.028 | 177430.7083 | 0.15346 | 0.17534 | 2569.2917 | 0.20394 | 93.9433 | 116.0953 | 1.8229 | 0 | [7 empty] | 43200 | 108083.1665 | inf | 108083.1665 | 108083.1665 | 5.4878e+27 | 54041.5833 | 99.522 | 74.761 | 74444.2168 | inf | 74444.2168 | 74444.2168 | 8.2125e+37 | 37222.1084 | 93.9433 | 71.9717 | Diode | 148.0591 | 101.9784
Text_B200_BatchSize16 | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949 | 1.7278 | 0.44897 | 1.2789 | 63.9437 | 1.8632 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 404 | 400 | 396 | 1.452 | 0.28179 | 1.3641 | 1.1783 | 0.26927 | 0.23807 | 1.4131 | 1.4407 | 1.4479 | 1.3619 | 1.0437 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 2.373e-05 | 0.034995 | 1.4758 | 1.4894 | 1.4717 | 1.4704 | 1.2692 | 1.491 | 1.5639 | 0.28993 | 0.34461 | 0.35356 | 0.11194 | 0.17089 | 0.17256 | 1.427 | 10.4133 | 2.1895 | 0.95265 | 6.6213 | 1.3901 | 1.3063 | 8.3257 | 1.7679 | 1.4044 | 21.2091 | 2.1983 | 1.2586 | 18.3784 | 1.9143 | 1.3432 | 19.7977 | 2.0498 | 1.3752 | 121.9861 | 2.1156 | 1.2787 | 111.6169 | 1.9384 | 1.3599 | 119.1032 | 2.0711 | 396 | 0.099207 | 1.0246 | 0.34813 | 1.3189 | 0.20744 | 1.483 | 0.33901 | 0.15368 | 0.69438 | 1.3932 | 1 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906 | 204.8693 | 217.7443 | 25 | 44.3459 | 195.7516 | 204.7673 | 25 | 42.196 | 193.7331 | 41.9812 | 180000.0417 | 192.7443 | 1.356 | 1.7889 | 179600.0417 | 4 | 395.9583 | 0.041667 | 204.9076 | 0.03783 | 0.013 | 177186.0417 | 1.3253 | 1.8782 | 2814 | 3.2861 | 192.7443 | 206.7932 | 1.7809 | 399.9583 | 11.8098 | 11.7871 | 12.2201 | 17.7853 | 13.186 | 203.2275 | 5.8517 | 180000 | 179.7673 | 0.28742 | 0.37669 | 179996.0833 | 3.875 | 0 | 0.041667 | 195.7538 | 0.03514 | 0.012 | 177174.75 | 0.28186 | 0.39369 | 2825.25 | 0.63643 | 179.7673 | 196.4253 | 1.5863 | 3.875 | 7.1094 | 7.2133 | 7.2133 | 7.2133 | 7.1699 | 198.7397 | 62.7268 | 43200 | 2113.284 | inf | 2113.284 | 2113.284 | 1.6781e+21 | 1056.8394 | 192.7443 | 121.3721 | 1637.3171 | inf | 1637.3171 | 1637.3171 | 1.2047e+32 | 818.6585 | 179.7673 | 114.8836 | Diode | 2.8949 | 2.2429
Text_B200_BatchSize32 | B_200 | 3600 | 1.5345 | 1.9612 | 0.41814 | 1.5345 | 1.2781 | 1.4353 | 81.3444 | 9.0909 | 808 | 3.492 | 1.8023 | 0.51502 | 1.2873 | 64.3644 | 1.9438 | 7.2608 | 7.54 | 1.6564 | 1.9 | 403 | 8.9104 | 0.076621 | 800 | 404 | 399.5 | 1.4803 | 0.74913 | 1.3336 | 0.41961 | 0.015152 | 0.27708 | 1.4725 | 1.5175 | 1.5183 | 1.2976 | 0.046048 | 0 | 0.15471 | 1.1689 | 97.1631 | 0.98678 | 0.44353 | 0.082978 | 0.17545 | 0.00078126 | 1.5984 | 1.5825 | 1.5516 | 1.5448 | 1.2739 | 1.6677 | 1.7418 | 0.37121 | 0.48323 | 0.49534 | 0.28747 | 0.31077 | 0.32568 | 1.4851 | 11.7657 | 2.4408 | 1.0538 | 7.6878 | 1.6157 | 1.3875 | 9.1944 | 1.9694 | 1.4813 | 23.3079 | 2.4228 | 1.423 | 21.8344 | 2.274 | 1.4263 | 21.8981 | 2.2708 | 1.4512 | 134.7761 | 2.3371 | 1.4362 | 132.224 | 2.2955 | 1.4368 | 132.1934 | 2.2943 | 417 | 0.14467 | 0.04352 | 0.025143 | 0.64199 | 0.011699 | 1.6019 | 0.48432 | 0.20738 | 0.75936 | 1.5345 | 1 | 735.9011 | 1915.2764 | 218.1728 | 444.7031 | 699.2431 | 914.8205 | 688.9342 | 57.192 | 74.2796 | 55.4482 | 46.4812 | 7.5607 | 0.049296 | 224.5887 | 235.6393 | 25 | 47.9558 | 214.4588 | 221.912 | 25 | 45.102 | 212.2235 | 44.4882 | 180000.0417 | 210.6393 | 1.5067 | 1.8776 | 179579.8333 | 20.2083 | 399.9583 | 0.041667 | 224.6318 | 0.053552 | 0.013 | 177520.8333 | 1.4703 | 1.9571 | 2479.2083 | 4.1134 | 210.6393 | 225.6918 | 3.1601 | 420.1667 | 12.2286 | 12.5095 | 13.0505 | 13.2579 | 12.5307 | 222.3051 | 12.0919 | 180000 | 196.912 | 0.3184 | 0.3947 | 179999.9583 | 0 | 0 | 0.041667 | 214.4613 | 0.058376 | 0.012 | 177392.625 | 0.31191 | 0.41125 | 2607.375 | 0.75998 | 196.912 | 215.2656 | 3.3289 | 0 | [7 empty] | 43200 | 1201.2783 | inf | 1201.2783 | 1201.2783 | 5.3834e+20 | 600.6846 | 210.6393 | 130.3196 | 923.0246 | inf | 923.0246 | 923.0246 | 4.2823e+31 | 461.5123 | 196.912 | 123.456 | Diode | 1.6456 | 1.2644
Text_B200_Deepspeedds_z1 | B_200 | 3600 | 1.3283 | 2 | 0.40753 | 1.3283 | 1.5057 | 1.4992 | 70.1844 | 7.9646 | 824 | 3.7532 | 1.7124 | 0.44076 | 1.2716 | 63.5803 | 1.9834 | 6.1758 | 6.4 | 2.5715 | 2 | 411 | 8.7335 | 0.9838 | 648 | 412 | 411.5 | 1.5056 | 0.87763 | 1.4238 | 1.1835 | 0.37444 | 0.60244 | 1.5252 | 1.5597 | 1.5687 | 1.3927 | 0.92206 | 0 | 29.0813 | 2.784 | 62.0211 | 5.59 | 0.43961 | 0.08395 | 0.59802 | 0.081701 | 1.431 | 1.4701 | 1.4443 | 1.4362 | 1.3595 | 1.727 | 1.8014 | 0.40709 | 0.52891 | 0.5415 | 0.31371 | 0.4753 | 0.47816 | 1.5196 | 11.8371 | 2.4584 | 1.1139 | 7.6479 | 1.6149 | 1.4347 | 9.0609 | 1.9384 | 1.5065 | 23.0756 | 2.3944 | 1.3444 | 19.0486 | 2.0051 | 1.4745 | 20.8606 | 2.1968 | 1.4921 | 129.3674 | 2.2654 | 1.4601 | 117.3759 | 2.0762 | 1.4803 | 126.4283 | 2.2171 | 5 | 0.44888 | 0.89333 | 0.27895 | 1.3299 | 0.28973 | 1.6774 | 0.63759 | 0.31233 | 0.79763 | 1.3283 | 1 | 658.807 | 1953.1287 | 195.3167 | 453.4919 | 599.3242 | 935.7165 | 719.5298 | 49.1733 | 75.9053 | 57.9123 | 46.9319 | 7.5826 | 0.048823 | 196.2231 | 210.994 | 25 | 43.2779 | 187.5467 | 197.4787 | 25 | 40.5817 | 185.6245 | 40.33 | 180000.0417 | 185.994 | 1.2903 | 1.8752 | 179583.9167 | 4.1667 | 408.375 | 3.5833 | 196.2594 | 0.037401 | 0.013 | 177912.0833 | 1.2481 | 1.9656 | 2087.9583 | 4.8861 | 185.994 | 198.1097 | 2.4213 | 416.0833 | 12.8913 | 12.8821 | 13.1489 | 20.5172 | 15.0557 | 195.4383 | 5.3496 | 180000 | 172.4787 | 0.27368 | 0.39574 | 179996.0833 | 3.875 | 0 | 0.041667 | 187.5488 | 0.035184 | 0.012 | 177932.375 | 0.26611 | 0.41345 | 2067.625 | 0.92553 | 172.4787 | 187.6966 | 2.2288 | 3.875 | 9.2376 | 9.3825 | 9.3825 | 9.3825 | 9.3249 | 190.4319 | 90.3303 | 43200 | 2642.9045 | inf | 2642.9045 | 2642.9045 | 1.4621e+21 | 1322.9082 | 185.994 | 117.997 | 2118.1977 | inf | 2118.1977 | 2118.1977 | 1.134e+32 | 1059.0989 | 172.4787 | 111.2393 | Diode | 3.6204 | 2.9016
Text_B200_Deepspeedds_z2 | B_200 | 3600 | 1.3723 | 1.887 | 0.41212 | 1.3723 | 1.3751 | 1.3605 | 74.5778 | 8.5714 | 815 | 3.0408 | 1.714 | 0.44392 | 1.2701 | 63.5059 | 1.8631 | 6.6051 | 6.9 | 2.1171 | 1.94 | 407 | 8.707 | 0.48509 | 415.5 | 407.5 | 396 | 1.4493 | 0.30285 | 1.3431 | 0.99899 | 0.22489 | 0.99439 | 1.3919 | 1.4448 | 1.4457 | 1.3407 | 0.83994 | 0 | 19.7537 | 2.5003 | 76.5089 | 0.77496 | 0.38857 | 0.073518 | 0.9943 | 0.032995 | 1.4565 | 1.4497 | 1.4443 | 1.4395 | 1.2118 | 1.4641 | 1.517 | 0.2956 | 0.34569 | 0.35482 | 0.13073 | 0.18442 | 0.18446 | 1.4251 | 10.343 | 2.1622 | 0.98144 | 6.6382 | 1.4007 | 1.2975 | 8.0329 | 1.7188 | 1.4141 | 21.083 | 2.1871 | 1.2807 | 18.207 | 1.9059 | 1.3448 | 19.3385 | 2.0169 | 1.3701 | 118.4675 | 2.0651 | 1.3502 | 111.2722 | 1.9515 | 1.3496 | 115.6842 | 2.0175 | 404 | 0.74163 | 0.82635 | 0.28124 | 1.3017 | 0.1572 | 1.4889 | 0.40617 | 0.56547 | 0.73709 | 1.3723 | 1 | 670.5766 | 1842.7441 | 198.8061 | 427.862 | 619.3966 | 875.0846 | 647.762 | 50.8145 | 71.1816 | 52.2643 | 46.9159 | 7.5819 | 0.048839 | 201.906 | 214.2379 | 25 | 43.6589 | 192.9388 | 201.4499 | 25 | 41.264 | 190.9526 | 40.7911 | 180000.0417 | 189.2379 | 1.3335 | 1.7761 | 179592.0417 | 12 | 395.9583 | 0.041667 | 201.9436 | 0.041055 | 0.013 | 177238.4583 | 1.3026 | 1.8819 | 2761.5833 | 3.3156 | 189.2379 | 203.7017 | 2.0173 | 407.9583 | 11.7107 | 11.7452 | 12.1925 | 16.5328 | 12.5003 | 200.2579 | 7.1847 | 180000 | 176.4499 | 0.28282 | 0.3742 | 179996.1667 | 3.7917 | 0 | 0.041667 | 192.9409 | 0.035993 | 0.012 | 177301.0833 | 0.27724 | 0.39528 | 2698.9167 | 0.64924 | 176.4499 | 193.4359 | 1.7082 | 3.7917 | 6.2284 | 6.278 | 6.278 | 6.278 | 6.2489 | 196.9944 | 54.741 | 43200 | 2372.9555 | inf | 2372.9555 | 2372.9555 | 2.0008e+21 | 1186.6001 | 189.2379 | 119.6189 | 1838.9034 | inf | 1838.9034 | 1838.9034 | 1.4165e+32 | 919.4517 | 176.4499 | 113.2249 | Diode | 3.2506 | 2.519
Text_B200_Deepspeedds_z3 | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949 | 1.7278 | 0.44897 | 1.2789 | 63.9437 | 1.8632 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 404 | 400 | 396 | 1.452 | 0.28179 | 1.3641 | 1.1783 | 0.26927 | 0.23807 | 1.4131 | 1.4407 | 1.4479 | 1.3619 | 1.0437 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 2.373e-05 | 0.034995 | 1.4758 | 1.4894 | 1.4717 | 1.4704 | 1.2692 | 1.491 | 1.5639 | 0.28993 | 0.34461 | 0.35356 | 0.11194 | 0.17089 | 0.17256 | 1.427 | 10.4133 | 2.1895 | 0.95265 | 6.6213 | 1.3901 | 1.3063 | 8.3257 | 1.7679 | 1.4044 | 21.2091 | 2.1983 | 1.2586 | 18.3784 | 1.9143 | 1.3432 | 19.7977 | 2.0498 | 1.3752 | 121.9861 | 2.1156 | 1.2787 | 111.6169 | 1.9384 | 1.3599 | 119.1032 | 2.0711 | 396 | 0.099207 | 1.0246 | 0.34813 | 1.3189 | 0.20744 | 1.483 | 0.33901 | 0.15368 | 0.69438 | 1.3932 | 1 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906 | 204.8693 | 217.7443 | 25 | 44.3459 | 195.7516 | 204.7673 | 25 | 42.196 | 193.7331 | 41.9812 | 180000.0417 | 192.7443 | 1.356 | 1.7889 | 179600.0417 | 4 | 395.9583 | 0.041667 | 204.9076 | 0.03783 | 0.013 | 177186.0417 | 1.3253 | 1.8782 | 2814 | 3.2861 | 192.7443 | 206.7932 | 1.7809 | 399.9583 | 11.8098 | 11.7871 | 12.2201 | 17.7853 | 13.186 | 203.2275 | 5.8517 | 180000 | 179.7673 | 0.28742 | 0.37669 | 179996.0833 | 3.875 | 0 | 0.041667 | 195.7538 | 0.03514 | 0.012 | 177174.75 | 0.28186 | 0.39369 | 2825.25 | 0.63643 | 179.7673 | 196.4253 | 1.5863 | 3.875 | 7.1094 | 7.2133 | 7.2133 | 7.2133 | 7.1699 | 198.7397 | 62.7268 | 43200 | 2113.284 | inf | 2113.284 | 2113.284 | 1.6781e+21 | 1056.8394 | 192.7443 | 121.3721 | 1637.3171 | inf | 1637.3171 | 1637.3171 | 1.2047e+32 | 818.6585 | 179.7673 | 114.8836 | Diode | 2.8949 | 2.2429
Text_B200_Lamma_1B | B_200 | 3600 | 0.82231 | 1.3127 | 0.40789 | 0.82231 | 1.5964 | 0.85262 | 48.12 | 4.4776 | 1599 | 2.3255 | 1.2043 | 0.43361 | 0.77068 | 38.5342 | 1.2993 | 2.171 | 2.28 | 2.3326 | 2.522 | 799 | 4.5037 | 0.15552 | 799.5 | 792 | 0 | 0.87897 | 0.0001482 | 0.82381 | 0.19878 | 0.016759 | 0.60963 | 0.85323 | 0.89746 | 0.89762 | 0.81808 | 0.064544 | 0 | 0.4565 | 1.1689 | 97.0705 | 0.59672 | 0.59764 | 0.10968 | 0.60963 | -0.008328 | 0.88475 | 0.84464 | 0.83481 | 0.82918 | 0.75827 | 0.67265 | 0.69452 | 0.33033 | 0.27661 | 0.28202 | 0.31881 | 0.27139 | 0.27718 | 0.88335 | 3.9515 | 0.84571 | 0.83758 | 3.4597 | 0.74312 | 0.84981 | 3.4692 | 0.74713 | 0.87458 | 7.6907 | 0.82208 | 0.84904 | 6.9839 | 0.75062 | 0.85011 | 6.9581 | 0.74729 | 0.85825 | 42.8502 | 0.76731 | 0.85185 | 42.0296 | 0.7536 | 0.85418 | 42.3604 | 0.75816 | 5 | 0.45858 | 0.059693 | 0.023626 | 0.12315 | 0.0066373 | 0.99762 | 0.24802 | 0.34082 | 0.48625 | 0.82231 | 1 | 407.3297 | 1281.9597 | 120.7612 | 297.6549 | 353.4174 | 581.3943 | 389.0648 | 29.4564 | 47.9867 | 31.8083 | 49.2121 | 7.6935 | 0.046561 | 126.0131 | 133.7276 | 25 | 26.1566 | 120.9148 | 125.1374 | 25 | 23.0587 | 119.7634 | 22.5235 | 180000.0417 | 108.7276 | 0.75741 | 1.1928 | 179208.0417 | 791.9583 | 0 | 0.041667 | 126.0329 | 0.045546 | 0.013 | 178972.1667 | 0.72836 | 1.2377 | 1027.875 | 5.8152 | 108.7276 | 126.89 | 6.3131 | 791.9583 | 7.1607 | 7.187 | 7.3985 | 7.8583 | 7.1943 | 126.3849 | 5.8911 | 180000 | 100.1374 | 0.1637 | 0.25561 | 179999.9583 | 0 | 0 | 0.041667 | 120.9159 | 0.037471 | 0.012 | 178979.375 | 0.15848 | 0.26511 | 1020.625 | 1.0797 | 100.1374 | 121.3065 | 4.8959 | 0 | [7 empty] | 43200 | 65689.7891 | inf | 65689.7891 | 65689.7891 | 1.0241e+25 | 32844.8998 | 108.7276 | 79.3638 | 52212.7906 | inf | 52212.7906 | 52212.7906 | 3.3034e+35 | 26106.3953 | 100.1374 | 75.0687 | Diode | 89.986 | 71.5244
Text_B200_Lamma_3B | B_200 | 3600 | 1.0446 | 1.6056 | 0.40919 | 1.0446 | 1.5371 | 1.1156 | 56.9089 | 6.8702 | 1039 | 2.5454 | 1.4823 | 0.42658 | 1.0557 | 52.7862 | 1.5852 | 4.2316 | 4.4 | 2.6954 | 2.7 | 519 | 6.9269 | 0.37202 | 520 | 515.5 | 515.5 | 1.1668 | 0.014885 | 1.1 | 0.40183 | 0.091413 | 0.57405 | 1.11 | 1.1917 | 1.1962 | 1.1003 | 0.3131 | 0 | 4.9876 | 1.7824 | 91.691 | 1.0999 | 0.38827 | 0.050956 | 0.5572 | 0.022894 | 1.1361 | 1.0931 | 1.0842 | 1.0807 | 0.98026 | 1.0225 | 1.0584 | 0.29133 | 0.28971 | 0.29606 | 0.27344 | 0.2349 | 0.24168 | 1.1611 | 7.108 | 1.4747 | 1.0456 | 5.5454 | 1.1949 | 1.0988 | 5.5792 | 1.2097 | 1.1536 | 13.6003 | 1.4408 | 1.0753 | 11.4538 | 1.2359 | 1.1118 | 11.7322 | 1.2728 | 1.1236 | 72.3215 | 1.3008 | 1.1133 | 69.8001 | 1.263 | 1.1138 | 70.9342 | 1.2804 | 5 | 0.41313 | 0.29962 | 0.10871 | 0.64633 | 0.071405 | 1.4613 | 0.22979 | 0.29859 | 0.56302 | 1.0446 | 1 | 523.0716 | 1568.0157 | 155.0752 | 364.0735 | 459.733 | 728.2121 | 520.2929 | 38.0228 | 59.6509 | 42.2472 | 48.0879 | 7.6388 | 0.047649 | 156.3431 | 166.2868 | 25 | 33.2793 | 149.6995 | 155.5338 | 25 | 29.9444 | 148.2133 | 29.3624 | 180000.0417 | 141.2868 | 0.98747 | 1.4874 | 179480.0833 | 508.6667 | 11.25 | 0.041667 | 156.3699 | 0.0381 | 0.013 | 178240.1667 | 0.95861 | 1.5809 | 1759.875 | 3.9111 | 141.2868 | 158.6439 | 2.9143 | 519.9167 | 9.5909 | 9.6022 | 9.9832 | 11.7182 | 9.7081 | 156.1889 | 5.822 | 180000 | 130.5338 | 0.21146 | 0.31579 | 179999.9583 | 0 | 0 | 0.041667 | 149.7011 | 0.034983 | 0.012 | 178237.375 | 0.20625 | 0.33381 | 1762.625 | 0.73841 | 130.5338 | 150.2968 | 2.5605 | 0 | [7 empty] | 43200 | 14274.0974 | inf | 14274.0974 | 14274.0974 | 1.0097e+23 | 7137.0997 | 141.2868 | 95.6434 | 11415.1231 | inf | 11415.1231 | 11415.1231 | 5.004e+33 | 5707.5615 | 130.5338 | 90.2669 | Diode | 19.5536 | 15.6372
Text_B200_Lamma_8B | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949 | 1.7278 | 0.44897 | 1.2789 | 63.9437 | 1.8632 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 404 | 400 | 396 | 1.452 | 0.28179 | 1.3641 | 1.1783 | 0.26927 | 0.23807 | 1.4131 | 1.4407 | 1.4479 | 1.3619 | 1.0437 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 2.373e-05 | 0.034995 | 1.4758 | 1.4894 | 1.4717 | 1.4704 | 1.2692 | 1.491 | 1.5639 | 0.28993 | 0.34461 | 0.35356 | 0.11194 | 0.17089 | 0.17256 | 1.427 | 10.4133 | 2.1895 | 0.95265 | 6.6213 | 1.3901 | 1.3063 | 8.3257 | 1.7679 | 1.4044 | 21.2091 | 2.1983 | 1.2586 | 18.3784 | 1.9143 | 1.3432 | 19.7977 | 2.0498 | 1.3752 | 121.9861 | 2.1156 | 1.2787 | 111.6169 | 1.9384 | 1.3599 | 119.1032 | 2.0711 | 396 | 0.099207 | 1.0246 | 0.34813 | 1.3189 | 0.20744 | 1.483 | 0.33901 | 0.15368 | 0.69438 | 1.3932 | 1 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906 | 204.8693 | 217.7443 | 25 | 44.3459 | 195.7516 | 204.7673 | 25 | 42.196 | 193.7331 | 41.9812 | 180000.0417 | 192.7443 | 1.356 | 1.7889 | 179600.0417 | 4 | 395.9583 | 0.041667 | 204.9076 | 0.03783 | 0.013 | 177186.0417 | 1.3253 | 1.8782 | 2814 | 3.2861 | 192.7443 | 206.7932 | 1.7809 | 399.9583 | 11.8098 | 11.7871 | 12.2201 | 17.7853 | 13.186 | 203.2275 | 5.8517 | 180000 | 179.7673 | 0.28742 | 0.37669 | 179996.0833 | 3.875 | 0 | 0.041667 | 195.7538 | 0.03514 | 0.012 | 177174.75 | 0.28186 | 0.39369 | 2825.25 | 0.63643 | 179.7673 | 196.4253 | 1.5863 | 3.875 | 7.1094 | 7.2133 | 7.2133 | 7.2133 | 7.1699 | 198.7397 | 62.7268 | 43200 | 2113.284 | inf | 2113.284 | 2113.284 | 1.6781e+21 | 1056.8394 | 192.7443 | 121.3721 | 1637.3171 | inf | 1637.3171 | 1637.3171 | 1.2047e+32 | 818.6585 | 179.7673 | 114.8836 | Diode | 2.8949 | 2.2429
Text_B200_SeqLength_1024 | B_200 | 3600 | 1.3928 | 1.8798 | 0.4125 | 1.3928 | 1.3497 | 1.3656 | 75.46 | 8.7379 | 792 | 3.1259 | 1.7269 | 0.44838 | 1.2785 | 63.9268 | 1.8636 | 6.8683 | 7.03 | 2.1257 | 2.04 | 396 | 8.994 | 0.3737 | 408 | 396 | 396 | 1.441 | 0.36164 | 1.3304 | 0.50101 | 0.18038 | 0.23982 | 1.4014 | 1.4428 | 1.4494 | 1.3233 | 0.65369 | 0 | 15.1867 | 2.5589 | 80.8655 | 0.9394 | 0.38934 | 0.06008 | 0.0075898 | 0.024434 | 1.4745 | 1.4635 | 1.4523 | 1.4463 | 1.2663 | 1.4989 | 1.5625 | 0.2959 | 0.34878 | 0.35793 | 0.12746 | 0.18394 | 0.18507 | 1.413 | 10.5406 | 2.1877 | 1.0008 | 6.7997 | 1.4356 | 1.3104 | 8.0961 | 1.7334 | 1.407 | 21.3716 | 2.2193 | 1.3076 | 18.7077 | 1.9597 | 1.3555 | 19.6456 | 2.0548 | 1.3764 | 119.2862 | 2.0866 | 1.3611 | 113.8063 | 1.9992 | 1.3625 | 117.0651 | 2.0431 | 396 | 0.10254 | 0.6382 | 0.21761 | 0.76309 | 0.12666 | 1.4661 | 0.33302 | 0.15859 | 0.68406 | 1.3928 | 1 | 678.8393 | 1835.7063 | 201.2557 | 426.2279 | 629.4087 | 871.2503 | 651.0014 | 51.6161 | 70.8822 | 52.5049 | 46.8606 | 7.5792 | 0.048897 | 204.7448 | 216.7736 | 25 | 44.155 | 195.6319 | 203.8488 | 25 | 41.7026 | 193.6144 | 41.3753 | 180000.0417 | 191.7736 | 1.3552 | 1.7884 | 179596.0417 | 8 | 395.9583 | 0.041667 | 204.7831 | 0.038737 | 0.013 | 177179.625 | 1.3243 | 1.8837 | 2820.4167 | 3.2967 | 191.7736 | 206.5746 | 1.837 | 403.9583 | 11.8126 | 11.8897 | 12.3268 | 15.9106 | 12.3377 | 203.1265 | 6.207 | 180000 | 178.8488 | 0.28729 | 0.37666 | 179996.3333 | 3.625 | 0 | 0.041667 | 195.6341 | 0.036997 | 0.012 | 177106.1667 | 0.28167 | 0.39599 | 2893.8333 | 0.63116 | 178.8488 | 196.3782 | 1.6674 | 3.625 | 5.4083 | 5.4244 | 5.4244 | 5.4244 | 5.411 | 200.7261 | 73.8226 | 43200 | 2181.9784 | inf | 2181.9784 | 2181.9784 | 1.7076e+21 | 1091.0772 | 191.7736 | 120.8868 | 1690.5041 | inf | 1690.5041 | 1690.5041 | 1.2272e+32 | 845.2521 | 178.8488 | 114.4244 | Diode | 2.989 | 2.3158
Text_B200_SeqLength_2048 | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949 | 1.7278 | 0.44897 | 1.2789 | 63.9437 | 1.8632 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 404 | 400 | 396 | 1.452 | 0.28179 | 1.3641 | 1.1783 | 0.26927 | 0.23807 | 1.4131 | 1.4407 | 1.4479 | 1.3619 | 1.0437 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 2.373e-05 | 0.034995 | 1.4758 | 1.4894 | 1.4717 | 1.4704 | 1.2692 | 1.491 | 1.5639 | 0.28993 | 0.34461 | 0.35356 | 0.11194 | 0.17089 | 0.17256 | 1.427 | 10.4133 | 2.1895 | 0.95265 | 6.6213 | 1.3901 | 1.3063 | 8.3257 | 1.7679 | 1.4044 | 21.2091 | 2.1983 | 1.2586 | 18.3784 | 1.9143 | 1.3432 | 19.7977 | 2.0498 | 1.3752 | 121.9861 | 2.1156 | 1.2787 | 111.6169 | 1.9384 | 1.3599 | 119.1032 | 2.0711 | 396 | 0.099207 | 1.0246 | 0.34813 | 1.3189 | 0.20744 | 1.483 | 0.33901 | 0.15368 | 0.69438 | 1.3932 | 1 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906 | 204.8693 | 217.7443 | 25 | 44.3459 | 195.7516 | 204.7673 | 25 | 42.196 | 193.7331 | 41.9812 | 180000.0417 | 192.7443 | 1.356 | 1.7889 | 179600.0417 | 4 | 395.9583 | 0.041667 | 204.9076 | 0.03783 | 0.013 | 177186.0417 | 1.3253 | 1.8782 | 2814 | 3.2861 | 192.7443 | 206.7932 | 1.7809 | 399.9583 | 11.8098 | 11.7871 | 12.2201 | 17.7853 | 13.186 | 203.2275 | 5.8517 | 180000 | 179.7673 | 0.28742 | 0.37669 | 179996.0833 | 3.875 | 0 | 0.041667 | 195.7538 | 0.03514 | 0.012 | 177174.75 | 0.28186 | 0.39369 | 2825.25 | 0.63643 | 179.7673 | 196.4253 | 1.5863 | 3.875 | 7.1094 | 7.2133 | 7.2133 | 7.2133 | 7.1699 | 198.7397 | 62.7268 | 43200 | 2113.284 | inf | 2113.284 | 2113.284 | 1.6781e+21 | 1056.8394 | 192.7443 | 121.3721 | 1637.3171 | inf | 1637.3171 | 1637.3171 | 1.2047e+32 | 818.6585 | 179.7673 | 114.8836 | Diode | 2.8949 | 2.2429
Text_B200_SeqLength_4096 | B_200 | 3600 | 1.394 | 1.8821 | 0.41118 | 1.394 | 1.3502 | 1.3675 | 75.2956 | 8.6538 | 792 | 3.1524 | 1.7277 | 0.44861 | 1.2791 | 63.953 | 1.8649 | 6.8543 | 6.985 | 2.1246 | 2.08 | 396 | 8.9789 | 0.43277 | 411.5 | 396.5 | 396 | 1.4345 | 0.34418 | 1.3355 | 0.59371 | 0.19904 | 0.8162 | 1.407 | 1.4379 | 1.4417 | 1.3297 | 0.73035 | 0 | 17.8616 | 2.5654 | 78.1502 | 0.98671 | 0.36748 | 0.068649 | 0.8162 | 0.035312 | 1.4761 | 1.4664 | 1.4541 | 1.4531 | 1.2208 | 1.4823 | 1.5313 | 0.29363 | 0.34498 | 0.35405 | 0.11691 | 0.1745 | 0.17456 | 1.4165 | 10.4936 | 2.1844 | 0.9734 | 6.6262 | 1.3985 | 1.3125 | 8.2021 | 1.7552 | 1.406 | 21.199 | 2.1975 | 1.2983 | 18.6655 | 1.9543 | 1.3569 | 19.6463 | 2.0501 | 1.377 | 120.144 | 2.0963 | 1.3624 | 114.0092 | 2.001 | 1.3628 | 117.2046 | 2.0457 | 400 | 0.60679 | 0.72367 | 0.2461 | 0.75657 | 0.13453 | 1.5104 | 0.38043 | 0.51021 | 0.72039 | 1.394 | 1 | 679.5989 | 1837.9769 | 201.4809 | 426.7551 | 630.0543 | 872.4869 | 651.9624 | 51.6662 | 70.9788 | 52.5811 | 46.8527 | 7.5788 | 0.048905 | 204.9353 | 217.3004 | 25 | 44.1867 | 195.813 | 204.2626 | 25 | 41.8141 | 193.7935 | 41.5276 | 180000.0417 | 192.3004 | 1.3566 | 1.7904 | 179596.125 | 7.9167 | 395.9583 | 0.041667 | 204.9737 | 0.039568 | 0.013 | 177209.9583 | 1.3259 | 1.8633 | 2790.0833 | 3.3096 | 192.3004 | 206.7996 | 1.9113 | 403.875 | 11.807 | 11.8603 | 12.2971 | 16.4076 | 12.5071 | 203.2508 | 6.6439 | 180000 | 179.2626 | 0.28757 | 0.37702 | 179996.25 | 3.7083 | 0 | 0.041667 | 195.8152 | 0.035485 | 0.012 | 177165.25 | 0.28198 | 0.39171 | 2834.75 | 0.6368 | 179.2626 | 196.5537 | 1.6046 | 3.7083 | 5.8726 | 5.8978 | 5.8978 | 5.8978 | 5.8792 | 200.5724 | 47.8563 | 43200 | 2144.4752 | inf | 2144.4752 | 2144.4752 | 1.6769e+21 | 1072.3416 | 192.3004 | 121.1502 | 1666.3055 | inf | 1666.3055 | 1666.3055 | 1.2063e+32 | 833.1528 | 179.2626 | 114.6313 | Diode | 2.9376 | 2.2826

## Load_characteristics
scenario | chip | duration_s | P_mean_MW | P_max_MW | P_min_MW | Energy_MWh | Peak_to_mean | Swing_p95_p05_MW | Time_at_high_load_pct | Dominant_period_s | Transitions_per_h | Ramp_p99_MW_per_s | P_high_level_MW | P_low_level_MW | Step_height_MW | Step_height_pct_rating | P_p999_MW | Dwell_high_mean_s | Dwell_high_p95_s | Dwell_low_mean_s | Dwell_low_p95_s | Bursts_per_h | Burst_period_mean_s | Burst_period_CV | Power_cycles_ge_10pct_per_h | Power_cycles_ge_30pct_per_h | Power_cycles_ge_50pct_per_h | Power_cycle_dP_max_MW | Damage_proxy_per_h | Swing_filtered_tau0.26s_MW | Swing_filtered_tau3.31s_MW | Swing_filtered_tau159s_MW | Max_change_in_0.1s_MW | Max_change_in_1s_MW | Max_change_in_5s_MW | Max_change_in_60s_MW | Swing_avg_1s_MW | Swing_avg_60s_MW | Swing_avg_900s_MW | Var_share_0_0.017Hz_pct | Var_share_0.017_0.1Hz_pct | Var_share_0.1_0.5Hz_pct | Var_share_0.5_0.8Hz_pct | Var_share_0.8_2Hz_pct | Var_share_2_25Hz_pct | Seam_jump_max_MW | Startup_60s_mean_minus_block_mean_MW | P_rms_MW | P_max_avg_60s_MW | P_max_avg_180s_MW | P_max_avg_300s_MW | Swing_period1s_max_MW | Swing_period1s_max_MW_x_E_MJ | Swing_period1s_max_MW_x_Prms_MW | Swing_period1s_mean_MW | Swing_period1s_mean_MW_x_E_MJ | Swing_period1s_mean_MW_x_Prms_MW | Swing_period1s_median_MW | Swing_period1s_median_MW_x_E_MJ | Swing_period1s_median_MW_x_Prms_MW | Swing_period5s_max_MW | Swing_period5s_max_MW_x_E_MJ | Swing_period5s_max_MW_x_Prms_MW | Swing_period5s_mean_MW | Swing_period5s_mean_MW_x_E_MJ | Swing_period5s_mean_MW_x_Prms_MW | Swing_period5s_median_MW | Swing_period5s_median_MW_x_E_MJ | Swing_period5s_median_MW_x_Prms_MW | Swing_period10s_max_MW | Swing_period10s_max_MW_x_E_MJ | Swing_period10s_max_MW_x_Prms_MW | Swing_period10s_mean_MW | Swing_period10s_mean_MW_x_E_MJ | Swing_period10s_mean_MW_x_Prms_MW | Swing_period10s_median_MW | Swing_period10s_median_MW_x_E_MJ | Swing_period10s_median_MW_x_Prms_MW | Swing_period60s_max_MW | Swing_period60s_max_MW_x_E_MJ | Swing_period60s_max_MW_x_Prms_MW | Swing_period60s_mean_MW | Swing_period60s_mean_MW_x_E_MJ | Swing_period60s_mean_MW_x_Prms_MW | Swing_period60s_median_MW | Swing_period60s_median_MW_x_E_MJ | Swing_period60s_median_MW_x_Prms_MW | ERCOT_changes_gt25pct_in_5s_per_h | LIPA_band_5_23.75Hz_amp_10s_MW | Ramp_max_MW_per_min | Variability_1min_std_MW | Swing_avg_4s_MW | Swing_avg_300s_MW | SoCo_band_0.1_0.5Hz_amp_60s_MW | SoCo_band_0.5_0.8Hz_amp_60s_MW | SoCo_band_0.8_2Hz_amp_60s_MW | Flicker_Pst_max_SCR20 | Peak_demand_15min_MW | Load_factor_15min
Image_H100_BatchSize_128 | H_100 | 3600 | 0.44828 | 0.86506 | 0.25337 | 0.44828 | 1.9298 | 0.58625 | 33.7089 | 16.0714 | 464 | 1.1514 | 0.81992 | 0.25577 | 0.56415 | 28.2077 | 0.86183 | 5.208 | 5.52 | 10.2948 | 11.213 | 231 | 15.5036 | 0.14852 | 232 | 24 | 0 | 0.60884 | 8.1173e-08 | 0.58469 | 0.40688 | 0.014932 | 0.16933 | 0.576 | 0.61062 | 0.61066 | 0.58385 | 0.039496 | 0 | 0.14094 | 76.0438 | 23.3736 | 0.37502 | 0.053716 | 0.012963 | 0.16758 | 0.0083248 | 0.51483 | 0.48853 | 0.46708 | 0.45534 | 0.51028 | 0.29333 | 0.30424 | 0.068075 | 0.037355 | 0.038272 | 0.0053346 | 0.0031312 | 0.0031314 | 0.60083 | 2.1948 | 0.45759 | 0.31942 | 0.86006 | 0.18525 | 0.39076 | 0.8852 | 0.19665 | 0.60856 | 3.368 | 0.37368 | 0.51323 | 2.4219 | 0.27197 | 0.57681 | 2.7095 | 0.30995 | 0.60222 | 16.4177 | 0.31328 | 0.58454 | 15.7244 | 0.30088 | 0.58338 | 15.927 | 0.30321 | 444 | 0.12854 | 0.037902 | 0.019296 | 0.55369 | 0.0012562 | 0.55703 | 0.10309 | 0.082359 | 0.2465 | 0.44828 | 1
Image_H100_BatchSize_256 | H_100 | 3600 | 0.43236 | 0.65396 | 0.25349 | 0.43236 | 1.5125 | 0.39229 | 45.1533 | 18 | 399 | 0.74254 | 0.64305 | 0.2576 | 0.38545 | 19.2726 | 0.65241 | 8.1003 | 8.38 | 9.9176 | 10.52 | 199 | 18.0179 | 0.10673 | 199.5 | 0 | 0 | 0.39869 | 5.8653e-11 | 0.39173 | 0.31897 | 0.012861 | 0.38697 | 0.38934 | 0.3966 | 0.39942 | 0.39148 | 0.038684 | 0 | 0.12143 | 86.4639 | 12.9889 | 0.36003 | 0.042305 | 0.023434 | 0.38624 | -0.014306 | 0.46951 | 0.45982 | 0.43813 | 0.4409 | 0.32803 | 0.1543 | 0.1571 | 0.039842 | 0.018344 | 0.018611 | 0.0049797 | 0.0028382 | 0.0028384 | 0.39437 | 1.1313 | 0.23194 | 0.18918 | 0.42564 | 0.089371 | 0.1867 | 0.36917 | 0.076648 | 0.39489 | 2.2136 | 0.2288 | 0.36723 | 1.6185 | 0.17237 | 0.38886 | 1.6773 | 0.1821 | 0.39438 | 10.7768 | 0.19372 | 0.39205 | 10.1707 | 0.18401 | 0.39235 | 10.0601 | 0.18218 | 0 | 0.28828 | 0.037438 | 0.019181 | 0.3888 | 0.0069119 | 0.46534 | 0.11444 | 0.20768 | 0.19598 | 0.43236 | 1
Image_H100_BatchSize_512 | H_100 | 3600 | 0.45261 | 1.1269 | 0.25307 | 0.45261 | 2.4897 | 0.85156 | 16.4356 | 14.0625 | 312 | 1.5462 | 1.1027 | 0.25847 | 0.84418 | 42.209 | 1.1243 | 3.32 | 3.34 | 17.5289 | 11 | 156 | 20.849 | 2.3419 | 243.5 | 156 | 0 | 0.86546 | 4.8191e-05 | 0.84731 | 0.44267 | 0.028347 | 0.63706 | 0.80482 | 0.87039 | 0.8734 | 0.84756 | 0.078641 | 0 | 0.24609 | 64.7699 | 34.2835 | 0.57758 | 0.078517 | 0.044399 | 0.41727 | -0.023391 | 0.53491 | 0.49933 | 0.47211 | 0.46975 | 0.74447 | 0.5535 | 0.57775 | 0.0884 | 0.057094 | 0.058843 | 0.01732 | 0.0063819 | 0.0063841 | 0.86424 | 3.5248 | 0.76065 | 0.37895 | 1.0998 | 0.24595 | 0.36296 | 0.67557 | 0.14309 | 0.86485 | 4.7121 | 0.56531 | 0.60892 | 2.9098 | 0.34146 | 0.59652 | 2.3787 | 0.24792 | 0.86191 | 25.2749 | 0.51628 | 0.68418 | 18.7906 | 0.37459 | 0.85502 | 23.0557 | 0.47411 | 156 | 0.47513 | 0.078641 | 0.031173 | 0.62119 | 0.028582 | 0.77105 | 0.18355 | 0.34052 | 0.45861 | 0.45261 | 1
Image_H100_ImageSize_16 | H_100 | 3600 | 0.36404 | 0.59557 | 0.25435 | 0.36404 | 1.636 | 0.32806 | 32.7044 | 12 | 599 | 0.62063 | 0.57686 | 0.25958 | 0.31728 | 15.864 | 0.59264 | 3.9323 | 4.16 | 8.0807 | 8.68 | 299 | 12.013 | 0.040278 | 299.5 | 0 | 0 | 0.33837 | 3.5755e-12 | 0.32649 | 0.18779 | 0.0066814 | 0.29585 | 0.32174 | 0.33639 | 0.33748 | 0.32552 | 0.0093232 | 0 | 0.12879 | 76.108 | 22.97 | 0.67663 | 0.093389 | 0.023176 | 0.26885 | -0.0013946 | 0.3897 | 0.36847 | 0.36601 | 0.36578 | 0.28686 | 0.12514 | 0.12789 | 0.049555 | 0.021045 | 0.021355 | 0.0030189 | 0.00095465 | 0.00095466 | 0.33272 | 0.83999 | 0.17219 | 0.22622 | 0.45857 | 0.095986 | 0.31666 | 0.57781 | 0.12261 | 0.33322 | 1.29 | 0.13804 | 0.32447 | 1.1815 | 0.12615 | 0.32536 | 1.2319 | 0.13159 | 0.33101 | 7.2414 | 0.1292 | 0.32754 | 7.1541 | 0.12764 | 0.32766 | 7.1602 | 0.12767 | 0 | 0.198 | 0.0069867 | 0.0033992 | 0.27873 | 0.0028278 | 0.27628 | 0.11906 | 0.17748 | 0.17125 | 0.36404 | 1
Image_H100_ImageSize_32 | H_100 | 3600 | 0.44828 | 0.86506 | 0.25337 | 0.44828 | 1.9298 | 0.58625 | 33.7089 | 16.0714 | 464 | 1.1514 | 0.81992 | 0.25577 | 0.56415 | 28.2077 | 0.86183 | 5.208 | 5.52 | 10.2948 | 11.213 | 231 | 15.5036 | 0.14852 | 232 | 24 | 0 | 0.60884 | 8.1173e-08 | 0.58469 | 0.40688 | 0.014932 | 0.16933 | 0.576 | 0.61062 | 0.61066 | 0.58385 | 0.039496 | 0 | 0.14094 | 76.0438 | 23.3736 | 0.37502 | 0.053716 | 0.012963 | 0.16758 | 0.0083248 | 0.51483 | 0.48853 | 0.46708 | 0.45534 | 0.51028 | 0.29333 | 0.30424 | 0.068075 | 0.037355 | 0.038272 | 0.0053346 | 0.0031312 | 0.0031314 | 0.60083 | 2.1948 | 0.45759 | 0.31942 | 0.86006 | 0.18525 | 0.39076 | 0.8852 | 0.19665 | 0.60856 | 3.368 | 0.37368 | 0.51323 | 2.4219 | 0.27197 | 0.57681 | 2.7095 | 0.30995 | 0.60222 | 16.4177 | 0.31328 | 0.58454 | 15.7244 | 0.30088 | 0.58338 | 15.927 | 0.30321 | 444 | 0.12854 | 0.037902 | 0.019296 | 0.55369 | 0.0012562 | 0.55703 | 0.10309 | 0.082359 | 0.2465 | 0.44828 | 1
Image_H100_ImageSize_64 | H_100 | 3600 | 0.8439 | 1.1874 | 0.25572 | 0.8439 | 1.407 | 0.9144 | 64.3933 | 21.9512 | 351 | 1.6475 | 1.1589 | 0.2651 | 0.89377 | 44.6885 | 1.1845 | 13.2267 | 14.14 | 7.3102 | 8.24 | 175 | 20.5369 | 0.18647 | 179.5 | 175.5 | 0 | 0.92459 | 0.00014327 | 0.9126 | 0.74691 | 0.027606 | 0.87537 | 0.88096 | 0.92104 | 0.92674 | 0.91221 | 0.094024 | 0 | 0.1568 | 89.7647 | 9.6777 | 0.31453 | 0.054986 | 0.031336 | 0.87522 | 0.04295 | 0.93717 | 0.90678 | 0.8609 | 0.86174 | 0.7889 | 0.6099 | 0.63928 | 0.086315 | 0.065208 | 0.067077 | 0.015454 | 0.017198 | 0.017198 | 0.9148 | 4.6521 | 0.96482 | 0.39504 | 1.4263 | 0.31429 | 0.16056 | 0.52788 | 0.11191 | 0.91768 | 9.6073 | 0.98484 | 0.69431 | 5.2189 | 0.58574 | 0.89897 | 5.582 | 0.67705 | 0.91583 | 48.5499 | 0.88539 | 0.90965 | 46.0597 | 0.85224 | 0.90885 | 45.5895 | 0.84897 | 329 | 0.65291 | 0.094024 | 0.043596 | 0.90726 | 0.018365 | 1.2776 | 0.2396 | 0.48035 | 0.44272 | 0.8439 | 1
Image_H100_ModelSize_128 | H_100 | 3600 | 0.44828 | 0.86506 | 0.25337 | 0.44828 | 1.9298 | 0.58625 | 33.7089 | 16.0714 | 464 | 1.1514 | 0.81992 | 0.25577 | 0.56415 | 28.2077 | 0.86183 | 5.208 | 5.52 | 10.2948 | 11.213 | 231 | 15.5036 | 0.14852 | 232 | 24 | 0 | 0.60884 | 8.1173e-08 | 0.58469 | 0.40688 | 0.014932 | 0.16933 | 0.576 | 0.61062 | 0.61066 | 0.58385 | 0.039496 | 0 | 0.14094 | 76.0438 | 23.3736 | 0.37502 | 0.053716 | 0.012963 | 0.16758 | 0.0083248 | 0.51483 | 0.48853 | 0.46708 | 0.45534 | 0.51028 | 0.29333 | 0.30424 | 0.068075 | 0.037355 | 0.038272 | 0.0053346 | 0.0031312 | 0.0031314 | 0.60083 | 2.1948 | 0.45759 | 0.31942 | 0.86006 | 0.18525 | 0.39076 | 0.8852 | 0.19665 | 0.60856 | 3.368 | 0.37368 | 0.51323 | 2.4219 | 0.27197 | 0.57681 | 2.7095 | 0.30995 | 0.60222 | 16.4177 | 0.31328 | 0.58454 | 15.7244 | 0.30088 | 0.58338 | 15.927 | 0.30321 | 444 | 0.12854 | 0.037902 | 0.019296 | 0.55369 | 0.0012562 | 0.55703 | 0.10309 | 0.082359 | 0.2465 | 0.44828 | 1
Image_H100_ModelSize_256 | H_100 | 3600 | 0.5448 | 1.1469 | 0.25563 | 0.5448 | 2.1051 | 0.87487 | 32.9644 | 28.125 | 255 | 1.5647 | 1.1221 | 0.25944 | 0.86265 | 43.1327 | 1.1422 | 9.2846 | 9.56 | 18.8965 | 20.58 | 127 | 28.1811 | 0.044136 | 127.5 | 127.5 | 0 | 0.8829 | 5.9539e-05 | 0.87371 | 0.78058 | 0.030465 | 0.87271 | 0.87319 | 0.8855 | 0.89021 | 0.87349 | 0.053991 | 0 | 0.066424 | 90.502 | 9.0844 | 0.27694 | 0.047383 | 0.022924 | 0.87022 | -0.016645 | 0.67069 | 0.61916 | 0.57505 | 0.55715 | 0.76021 | 0.57129 | 0.5994 | 0.058159 | 0.041165 | 0.042551 | 0.0010759 | 0.00028063 | 0.00028063 | 0.87815 | 4.2644 | 0.88587 | 0.27929 | 0.95004 | 0.21013 | 0.024484 | 0.09886 | 0.019772 | 0.8788 | 8.9559 | 0.91924 | 0.54996 | 3.7979 | 0.4249 | 0.83247 | 3.9365 | 0.49159 | 0.87833 | 30.6137 | 0.62119 | 0.87475 | 28.5948 | 0.58644 | 0.87414 | 27.8259 | 0.57366 | 255 | 0.6494 | 0.053991 | 0.02102 | 0.86959 | 0.007305 | 0.68028 | 0.26681 | 0.46815 | 0.40983 | 0.5448 | 1
Image_H100_ModelSize_512 | H_100 | 3600 | 0.55789 | 1.349 | 0.25497 | 0.55789 | 2.418 | 1.0543 | 28.5533 | 81.8182 | 88 | 1.0896 | 1.2993 | 0.25869 | 1.0406 | 52.0296 | 1.3212 | 23.3395 | 25.594 | 58.4218 | 61.84 | 43 | 81.535 | 0.029494 | 48 | 44 | 44 | 1.0601 | 0.00055529 | 1.0508 | 1.0441 | 0.098107 | 0.16602 | 0.9855 | 1.0578 | 1.0938 | 1.0505 | 0.37834 | 0 | 62.8663 | 32.8057 | 4.2261 | 0.080502 | 0.012778 | 0.00858 | 0.011512 | -0.068003 | 0.72515 | 0.70994 | 0.65314 | 0.59161 | 0.87473 | 0.75514 | 0.79558 | 0.030792 | 0.02575 | 0.026538 | 0.00033882 | 8.883e-05 | 8.883e-05 | 1.0504 | 5.6937 | 1.1768 | 0.12818 | 0.46689 | 0.10594 | 0.0019482 | 0.0025637 | 0.00051273 | 1.0521 | 11.2906 | 1.206 | 0.24767 | 1.994 | 0.22639 | 0.0053648 | 0.014165 | 0.0014165 | 1.0576 | 42.0778 | 0.87682 | 0.98753 | 34.1523 | 0.72526 | 1.0547 | 40.4271 | 0.8536 | 88 | 0.12345 | 0.3744 | 0.19812 | 1.0489 | 0.036425 | 0.74882 | 0.13263 | 0.1022 | 0.24709 | 0.55789 | 1
Text_H100_BatchSize2 | H_100 | 3600 | 0.55738 | 0.65601 | 0.25271 | 0.55738 | 1.177 | 0.36095 | 88.9067 | 45 | 176 | 0.46491 | 0.59233 | 0.25998 | 0.33235 | 16.6176 | 0.64906 | 36.5216 | 43.42 | 4.2636 | 4.82 | 87 | 40.6368 | 0.30187 | 84 | 0 | 0 | 0.39329 | 9.0691e-12 | 0.35188 | 0.21361 | 0.068828 | 0.050787 | 0.32426 | 0.39155 | 0.39598 | 0.34679 | 0.24094 | 0 | 44.0966 | 33.5729 | 21.1307 | 0.99992 | 0.13405 | 0.065896 | 0.011709 | 0.017193 | 0.56561 | 0.58531 | 0.57809 | 0.57904 | 0.28648 | 0.12758 | 0.12985 | 0.034862 | 0.018242 | 0.018312 | 0.022304 | 0.013099 | 0.0131 | 0.36643 | 0.98393 | 0.20141 | 0.097972 | 0.25564 | 0.052003 | 0.050693 | 0.14844 | 0.029695 | 0.3663 | 1.9266 | 0.19672 | 0.13545 | 0.71722 | 0.072958 | 0.058748 | 0.34655 | 0.034669 | 0.34772 | 10.3388 | 0.17422 | 0.22248 | 7.3051 | 0.12327 | 0.18222 | 6.3515 | 0.10649 | 0 | 0.041512 | 0.2302 | 0.082131 | 0.23371 | 0.054527 | 0.33566 | 0.098021 | 0.04294 | 0.11115 | 0.55738 | 1
Text_H100_BatchSize16 | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414 | 1.2625 | 0.28308 | 0.97944 | 48.972 | 1.3829 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 536 | 268 | 267.5 | 1.1045 | 0.0033464 | 0.99286 | 0.39238 | 0.01274 | 0.17007 | 1.0839 | 1.13 | 1.1336 | 0.96631 | 0.051026 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.11151 | 0.012483 | 1.1458 | 1.1321 | 1.1154 | 1.1105 | 0.93885 | 0.83033 | 0.86975 | 0.21342 | 0.19613 | 0.20093 | 0.085967 | 0.099804 | 0.10017 | 1.098 | 6.3489 | 1.3214 | 0.5986 | 2.9839 | 0.63118 | 0.47019 | 2.8106 | 0.5681 | 1.1093 | 12.5723 | 1.295 | 0.91949 | 9.991 | 1.0414 | 1.0467 | 11.027 | 1.1613 | 1.0736 | 71.9283 | 1.243 | 1.0582 | 70.0547 | 1.2124 | 1.0589 | 70.4741 | 1.2139 | 284 | 0.089418 | 0.051026 | 0.036818 | 0.53716 | 0.0091664 | 1.1001 | 0.28913 | 0.15812 | 0.51407 | 1.1033 | 1
Text_H100_BatchSize32 | H_100 | 3600 | 1.1534 | 1.4317 | 0.26503 | 1.1534 | 1.2413 | 1.0996 | 87.36 | 14.2857 | 503 | 2.5218 | 1.2966 | 0.28786 | 1.0087 | 50.4356 | 1.415 | 12.5153 | 12.84 | 1.7927 | 1.96 | 251 | 14.308 | 0.045065 | 516 | 251.5 | 251.5 | 1.1306 | 0.006143 | 1.0055 | 0.37541 | 0.010074 | 0.72363 | 1.1236 | 1.1646 | 1.1667 | 0.9652 | 0.036478 | 0 | 0.062454 | 35.0869 | 62.2372 | 1.967 | 0.54333 | 0.10309 | 0.61738 | -0.011063 | 1.193 | 1.1783 | 1.1637 | 1.1595 | 0.99259 | 0.86874 | 0.91612 | 0.22136 | 0.21537 | 0.22045 | 0.10294 | 0.12555 | 0.12559 | 1.1342 | 6.4419 | 1.3335 | 0.60785 | 3.2149 | 0.67751 | 0.43526 | 2.7149 | 0.54634 | 1.1219 | 13.2901 | 1.3669 | 0.9065 | 10.2546 | 1.0661 | 1.0825 | 11.7933 | 1.2367 | 1.1072 | 77.6101 | 1.3356 | 1.0939 | 75.6983 | 1.305 | 1.0939 | 75.5395 | 1.3033 | 284 | 0.45683 | 0.027611 | 0.014914 | 0.49199 | 0.0017868 | 1.2555 | 0.25804 | 0.34228 | 0.55623 | 1.1534 | 1
Text_H100_Deepspeedds_z1 | H_100 | 3600 | 1.0289 | 1.4743 | 0.25423 | 1.0289 | 1.433 | 1.1809 | 73.1756 | 13.0435 | 1104 | 2.8028 | 1.2893 | 0.28568 | 1.0036 | 50.1806 | 1.4626 | 4.7976 | 8.81 | 1.7197 | 2.96 | 551 | 6.5102 | 0.43421 | 1348.5 | 296 | 276 | 1.1852 | 0.018295 | 1.1443 | 0.48911 | 0.027587 | 0.31489 | 1.1849 | 1.2102 | 1.2102 | 1.1351 | 0.072364 | 0 | 0.15517 | 45.5815 | 51.7663 | 1.9907 | 0.44603 | 0.060206 | 0.27463 | -0.012042 | 1.1012 | 1.0756 | 1.0467 | 1.0474 | 1.0758 | 1.0012 | 1.0582 | 0.39678 | 0.40523 | 0.41427 | 0.36804 | 0.40461 | 0.40769 | 1.188 | 6.7237 | 1.4069 | 0.87622 | 4.2619 | 0.91509 | 0.95306 | 4.432 | 0.94571 | 1.1883 | 13.5635 | 1.41 | 1.1044 | 11.2576 | 1.2069 | 1.1791 | 11.4444 | 1.2428 | 1.1842 | 75.4798 | 1.3334 | 1.1809 | 72.8954 | 1.3002 | 1.1808 | 72.9234 | 1.3006 | 164 | 0.20176 | 0.045084 | 0.0306 | 0.6815 | 0.017051 | 1.2069 | 0.4699 | 0.19153 | 0.59769 | 1.0289 | 1
Text_H100_Deepspeedds_z2 | H_100 | 3600 | 1.0739 | 1.3964 | 0.25979 | 1.0739 | 1.3003 | 1.0442 | 84.7 | 13.4328 | 559 | 2.1255 | 1.2388 | 0.28116 | 0.95762 | 47.8808 | 1.3718 | 10.9229 | 11.56 | 1.9639 | 2.14 | 279 | 12.8576 | 0.14207 | 559.5 | 279.5 | 260 | 1.102 | 0.0027368 | 0.98334 | 0.39751 | 0.016255 | 0.98353 | 1.0746 | 1.1284 | 1.1285 | 0.97557 | 0.055001 | 0 | 0.3005 | 45.118 | 51.8542 | 2.128 | 0.42275 | 0.17648 | 0.9523 | -0.011038 | 1.1178 | 1.1042 | 1.0874 | 1.084 | 0.96489 | 0.81023 | 0.86307 | 0.22437 | 0.20504 | 0.20995 | 0.098816 | 0.11192 | 0.11212 | 1.0869 | 6.0524 | 1.2566 | 0.60237 | 2.9276 | 0.61984 | 0.53191 | 3.0929 | 0.62597 | 1.0904 | 12.1981 | 1.2632 | 0.93465 | 9.9263 | 1.0353 | 1.0248 | 10.5911 | 1.11 | 1.0571 | 69.2645 | 1.1962 | 1.0437 | 67.2468 | 1.1665 | 1.0434 | 67.1018 | 1.1698 | 289 | 0.70629 | 0.036912 | 0.028889 | 0.54644 | 0.004097 | 1.2657 | 0.29925 | 0.52408 | 0.58555 | 1.0739 | 1
Text_H100_Deepspeedds_z3 | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414 | 1.2625 | 0.28308 | 0.97944 | 48.972 | 1.3829 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 536 | 268 | 267.5 | 1.1045 | 0.0033464 | 0.99286 | 0.39238 | 0.01274 | 0.17007 | 1.0839 | 1.13 | 1.1336 | 0.96631 | 0.051026 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.11151 | 0.012483 | 1.1458 | 1.1321 | 1.1154 | 1.1105 | 0.93885 | 0.83033 | 0.86975 | 0.21342 | 0.19613 | 0.20093 | 0.085967 | 0.099804 | 0.10017 | 1.098 | 6.3489 | 1.3214 | 0.5986 | 2.9839 | 0.63118 | 0.47019 | 2.8106 | 0.5681 | 1.1093 | 12.5723 | 1.295 | 0.91949 | 9.991 | 1.0414 | 1.0467 | 11.027 | 1.1613 | 1.0736 | 71.9283 | 1.243 | 1.0582 | 70.0547 | 1.2124 | 1.0589 | 70.4741 | 1.2139 | 284 | 0.089418 | 0.051026 | 0.036818 | 0.53716 | 0.0091664 | 1.1001 | 0.28913 | 0.15812 | 0.51407 | 1.1033 | 1
Text_H100_Lamma_1B | H_100 | 3600 | 0.69104 | 1.1725 | 0.25212 | 0.69104 | 1.6967 | 0.86267 | 50.7711 | 4.9451 | 1423 | 2.0909 | 1.08 | 0.2935 | 0.78649 | 39.3245 | 1.1536 | 2.5587 | 2.65 | 2.4997 | 2.58 | 711 | 5.0585 | 0.19477 | 712 | 711.5 | 0 | 0.88674 | 0.00017696 | 0.84092 | 0.22084 | 0.032148 | 0.47909 | 0.87544 | 0.91343 | 0.91444 | 0.84638 | 0.095069 | 0 | 1.1207 | 1.447 | 95.5842 | 0.887 | 0.89019 | 0.0709 | 0.47909 | 0.0067453 | 0.76554 | 0.71654 | 0.70894 | 0.70522 | 0.78025 | 0.57308 | 0.6065 | 0.30221 | 0.20903 | 0.21513 | 0.29701 | 0.19458 | 0.19948 | 0.89743 | 3.1997 | 0.70648 | 0.84677 | 2.9474 | 0.65146 | 0.8579 | 2.995 | 0.66296 | 0.88748 | 6.402 | 0.70435 | 0.85041 | 5.9188 | 0.65418 | 0.86011 | 6.0104 | 0.66477 | 0.86836 | 36.622 | 0.67428 | 0.86249 | 35.762 | 0.6601 | 0.86199 | 36.1263 | 0.66417 | 5 | 0.35874 | 0.082535 | 0.029563 | 0.22136 | 0.02233 | 1.0156 | 0.26116 | 0.29423 | 0.47279 | 0.69104 | 1
Text_H100_Lamma_3B | H_100 | 3600 | 0.91685 | 1.3174 | 0.25419 | 0.91685 | 1.4368 | 0.99294 | 72.2444 | 8.2569 | 856 | 2.2317 | 1.2073 | 0.2662 | 0.94111 | 47.0557 | 1.2951 | 6.0707 | 6.26 | 2.345 | 2.36 | 427 | 8.4043 | 0.20018 | 428 | 428 | 96 | 1.0366 | 0.0016038 | 0.97785 | 0.36748 | 0.061858 | 0.34175 | 1.0005 | 1.0533 | 1.0534 | 0.98058 | 0.21494 | 0 | 3.4802 | 3.5882 | 90.8855 | 1.6989 | 0.29457 | 0.052616 | 0.34042 | 0.00078832 | 0.98781 | 0.96062 | 0.94011 | 0.94088 | 0.87262 | 0.72366 | 0.75255 | 0.22557 | 0.17788 | 0.18321 | 0.10328 | 0.090036 | 0.0903 | 1.0306 | 5.5189 | 1.1449 | 0.82641 | 3.6828 | 0.79131 | 0.96743 | 3.7882 | 0.83914 | 1.0212 | 10.1107 | 1.0738 | 0.97634 | 9.0325 | 0.96744 | 0.98891 | 9.3073 | 0.98795 | 1.0015 | 56.7521 | 1.0064 | 0.99234 | 54.5921 | 0.97961 | 0.99447 | 55.2556 | 0.98694 | 433 | 0.25398 | 0.18446 | 0.066887 | 0.59685 | 0.044455 | 1.1874 | 0.27896 | 0.20935 | 0.48663 | 0.91685 | 1
Text_H100_Lamma_8B | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414 | 1.2625 | 0.28308 | 0.97944 | 48.972 | 1.3829 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 536 | 268 | 267.5 | 1.1045 | 0.0033464 | 0.99286 | 0.39238 | 0.01274 | 0.17007 | 1.0839 | 1.13 | 1.1336 | 0.96631 | 0.051026 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.11151 | 0.012483 | 1.1458 | 1.1321 | 1.1154 | 1.1105 | 0.93885 | 0.83033 | 0.86975 | 0.21342 | 0.19613 | 0.20093 | 0.085967 | 0.099804 | 0.10017 | 1.098 | 6.3489 | 1.3214 | 0.5986 | 2.9839 | 0.63118 | 0.47019 | 2.8106 | 0.5681 | 1.1093 | 12.5723 | 1.295 | 0.91949 | 9.991 | 1.0414 | 1.0467 | 11.027 | 1.1613 | 1.0736 | 71.9283 | 1.243 | 1.0582 | 70.0547 | 1.2124 | 1.0589 | 70.4741 | 1.2139 | 284 | 0.089418 | 0.051026 | 0.036818 | 0.53716 | 0.0091664 | 1.1001 | 0.28913 | 0.15812 | 0.51407 | 1.1033 | 1
Text_H100_SeqLength_1024 | H_100 | 3600 | 1.1028 | 1.4045 | 0.25894 | 1.1028 | 1.2736 | 1.0592 | 85.7133 | 6.6667 | 544 | 2.1698 | 1.262 | 0.28835 | 0.97368 | 48.6841 | 1.3842 | 11.3757 | 11.62 | 1.8841 | 2.14 | 271 | 13.2338 | 0.064134 | 544 | 272 | 268 | 1.1104 | 0.0032345 | 0.98584 | 0.38872 | 0.014448 | 0.16622 | 1.0861 | 1.136 | 1.1383 | 0.9556 | 0.045023 | 0 | 0.15489 | 44.8184 | 52.5946 | 1.9177 | 0.42111 | 0.093287 | 0.050748 | -0.01679 | 1.1448 | 1.1369 | 1.1181 | 1.114 | 0.95477 | 0.80745 | 0.86032 | 0.2147 | 0.197 | 0.20193 | 0.086711 | 0.10282 | 0.10289 | 1.0985 | 5.9312 | 1.256 | 0.60175 | 3.0093 | 0.63575 | 0.48973 | 2.8766 | 0.58167 | 1.0996 | 11.9854 | 1.2579 | 0.8941 | 9.6647 | 1.0084 | 1.0439 | 10.9843 | 1.1544 | 1.072 | 71.7941 | 1.2367 | 1.0581 | 70.0069 | 1.2112 | 1.0566 | 69.8519 | 1.2116 | 285 | 0.058418 | 0.038468 | 0.030738 | 0.52758 | 0.0092602 | 1.1013 | 0.28277 | 0.16407 | 0.51177 | 1.1028 | 1
Text_H100_SeqLength_2048 | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414 | 1.2625 | 0.28308 | 0.97944 | 48.972 | 1.3829 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 536 | 268 | 267.5 | 1.1045 | 0.0033464 | 0.99286 | 0.39238 | 0.01274 | 0.17007 | 1.0839 | 1.13 | 1.1336 | 0.96631 | 0.051026 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.11151 | 0.012483 | 1.1458 | 1.1321 | 1.1154 | 1.1105 | 0.93885 | 0.83033 | 0.86975 | 0.21342 | 0.19613 | 0.20093 | 0.085967 | 0.099804 | 0.10017 | 1.098 | 6.3489 | 1.3214 | 0.5986 | 2.9839 | 0.63118 | 0.47019 | 2.8106 | 0.5681 | 1.1093 | 12.5723 | 1.295 | 0.91949 | 9.991 | 1.0414 | 1.0467 | 11.027 | 1.1613 | 1.0736 | 71.9283 | 1.243 | 1.0582 | 70.0547 | 1.2124 | 1.0589 | 70.4741 | 1.2139 | 284 | 0.089418 | 0.051026 | 0.036818 | 0.53716 | 0.0091664 | 1.1001 | 0.28913 | 0.15812 | 0.51407 | 1.1033 | 1
Text_H100_SeqLength_4096 | H_100 | 3600 | 1.1002 | 1.4021 | 0.26093 | 1.1002 | 1.2744 | 1.0597 | 85.56 | 13.4328 | 536 | 2.2411 | 1.2627 | 0.28145 | 0.98121 | 49.0603 | 1.3823 | 11.4909 | 11.72 | 1.9346 | 2.08 | 267 | 13.41 | 0.02735 | 552 | 268 | 267.5 | 1.1122 | 0.0033674 | 0.99385 | 0.39724 | 0.01131 | 0.18958 | 1.0907 | 1.1336 | 1.1339 | 0.96827 | 0.048835 | 0 | 0.052026 | 45.5774 | 51.8231 | 2.0413 | 0.41035 | 0.095876 | 0.032359 | 0.0063762 | 1.1432 | 1.1297 | 1.1105 | 1.1073 | 0.91822 | 0.81736 | 0.85558 | 0.21626 | 0.1994 | 0.20427 | 0.084774 | 0.10161 | 0.10199 | 1.0987 | 6.133 | 1.2951 | 0.58944 | 2.9189 | 0.61795 | 0.4708 | 2.7695 | 0.55689 | 1.1047 | 12.9109 | 1.3277 | 0.89804 | 9.6857 | 1.0114 | 1.0471 | 11.0357 | 1.1581 | 1.0741 | 71.8121 | 1.2413 | 1.0588 | 69.8946 | 1.2103 | 1.0592 | 70.4496 | 1.2145 | 284 | 0.078369 | 0.047343 | 0.034159 | 0.54216 | 0.0075173 | 1.1128 | 0.28835 | 0.16178 | 0.51406 | 1.1002 | 1
Image_B200_BatchSize_128 | B_200 | 3600 | 0.65184 | 1.2119 | 0.40032 | 0.65184 | 1.8592 | 0.79231 | 30.1867 | 11.3924 | 632 | 1.5165 | 1.1848 | 0.40683 | 0.77801 | 38.9003 | 1.2087 | 3.422 | 3.48 | 7.9642 | 8.78 | 316 | 11.3863 | 0.05211 | 316 | 316 | 0 | 0.80717 | 2.4154e-05 | 0.78943 | 0.41217 | 0.01155 | 0.11376 | 0.77468 | 0.80821 | 0.81004 | 0.78852 | 0.034987 | 0 | 0.047497 | 73.9386 | 25.4308 | 0.50986 | 0.058211 | 0.014977 | 0.066578 | -0.013138 | 0.72825 | 0.68413 | 0.66325 | 0.65814 | 0.70353 | 0.59361 | 0.6144 | 0.12439 | 0.099498 | 0.10146 | 0.015915 | 0.012465 | 0.012465 | 0.80481 | 3.7643 | 0.79091 | 0.57108 | 2.0831 | 0.45047 | 0.75805 | 2.5085 | 0.56343 | 0.8016 | 5.5168 | 0.61245 | 0.78966 | 5.1485 | 0.574 | 0.79101 | 5.3351 | 0.59449 | 0.79636 | 31.9816 | 0.59563 | 0.79131 | 30.9483 | 0.57618 | 0.79133 | 30.8123 | 0.57406 | 316 | 0.049924 | 0.033398 | 0.018919 | 0.64822 | 0.0032829 | 0.66222 | 0.12879 | 0.074954 | 0.35899 | 0.65184 | 1
Image_B200_BatchSize_256 | B_200 | 3600 | 0.64912 | 1.3949 | 0.40261 | 0.64912 | 2.149 | 0.96041 | 23.8711 | 11.1111 | 647 | 1.9164 | 1.3559 | 0.40712 | 0.9488 | 47.44 | 1.3779 | 2.6435 | 2.68 | 8.4886 | 9.28 | 323 | 11.1321 | 0.072785 | 323.5 | 323.5 | 0 | 0.97398 | 0.00073691 | 0.95352 | 0.4306 | 0.01206 | 0.96465 | 0.96469 | 0.99052 | 0.99115 | 0.95359 | 0.044256 | 0 | 0.032596 | 62.7865 | 35.5695 | 1.4669 | 0.10555 | 0.038932 | 0.96358 | 0.019454 | 0.74285 | 0.67741 | 0.66131 | 0.65773 | 0.84547 | 0.7782 | 0.81006 | 0.15442 | 0.13573 | 0.13915 | 0.027811 | 0.015397 | 0.015402 | 0.97224 | 4.516 | 0.97666 | 0.62976 | 2.3875 | 0.52699 | 0.90402 | 2.9189 | 0.65979 | 0.97216 | 6.6065 | 0.75126 | 0.94917 | 6.1743 | 0.70504 | 0.95924 | 6.4291 | 0.7368 | 0.96307 | 38.8512 | 0.73986 | 0.95991 | 37.386 | 0.71285 | 0.96073 | 36.789 | 0.70128 | 321 | 0.71892 | 0.044256 | 0.028758 | 0.63817 | 0.0035978 | 1.1542 | 0.25897 | 0.52473 | 0.54698 | 0.64912 | 1
Image_B200_BatchSize_512 | B_200 | 3600 | 0.65202 | 1.5094 | 0.40186 | 0.65202 | 2.315 | 1.0803 | 20.5644 | 11.1111 | 656 | 2.2058 | 1.4706 | 0.4073 | 1.0633 | 53.1653 | 1.5038 | 2.2571 | 2.3 | 8.7276 | 9.1 | 328 | 10.9847 | 0.035334 | 328 | 328 | 328 | 1.0962 | 0.0060867 | 1.0623 | 0.42889 | 0.011989 | 0.14876 | 1.0609 | 1.1051 | 1.1051 | 1.0577 | 0.044266 | 0 | 0.018962 | 57.9039 | 40.8257 | 1.1347 | 0.090152 | 0.026503 | 0.0032195 | 0.019106 | 0.75361 | 0.67734 | 0.66247 | 0.65941 | 0.95025 | 0.94492 | 0.98561 | 0.18051 | 0.16936 | 0.17406 | 0.038509 | 0.022855 | 0.022859 | 1.0972 | 5.0355 | 1.1076 | 0.6848 | 2.6333 | 0.58905 | 0.98844 | 3.4458 | 0.79432 | 1.0937 | 7.4013 | 0.85147 | 1.0628 | 6.9492 | 0.80199 | 1.0797 | 7.2352 | 0.83745 | 1.0852 | 43.876 | 0.84469 | 1.08 | 42.25 | 0.81361 | 1.0801 | 42.277 | 0.81108 | 328 | 0.085618 | 0.042927 | 0.031857 | 0.62529 | 0.0059627 | 1.0928 | 0.21384 | 0.08384 | 0.51733 | 0.65202 | 1
Image_B200_ImageSize_32 | B_200 | 3600 | 0.65184 | 1.2119 | 0.40032 | 0.65184 | 1.8592 | 0.79231 | 30.1867 | 11.3924 | 632 | 1.5165 | 1.1848 | 0.40683 | 0.77801 | 38.9003 | 1.2087 | 3.422 | 3.48 | 7.9642 | 8.78 | 316 | 11.3863 | 0.05211 | 316 | 316 | 0 | 0.80717 | 2.4154e-05 | 0.78943 | 0.41217 | 0.01155 | 0.11376 | 0.77468 | 0.80821 | 0.81004 | 0.78852 | 0.034987 | 0 | 0.047497 | 73.9386 | 25.4308 | 0.50986 | 0.058211 | 0.014977 | 0.066578 | -0.013138 | 0.72825 | 0.68413 | 0.66325 | 0.65814 | 0.70353 | 0.59361 | 0.6144 | 0.12439 | 0.099498 | 0.10146 | 0.015915 | 0.012465 | 0.012465 | 0.80481 | 3.7643 | 0.79091 | 0.57108 | 2.0831 | 0.45047 | 0.75805 | 2.5085 | 0.56343 | 0.8016 | 5.5168 | 0.61245 | 0.78966 | 5.1485 | 0.574 | 0.79101 | 5.3351 | 0.59449 | 0.79636 | 31.9816 | 0.59563 | 0.79131 | 30.9483 | 0.57618 | 0.79133 | 30.8123 | 0.57406 | 316 | 0.049924 | 0.033398 | 0.018919 | 0.64822 | 0.0032829 | 0.66222 | 0.12879 | 0.074954 | 0.35899 | 0.65184 | 1
Image_B200_ImageSize_64 | B_200 | 3600 | 1.0173 | 1.5695 | 0.4055 | 1.0173 | 1.5429 | 1.126 | 52.9178 | 18.3673 | 392 | 2.073 | 1.5275 | 0.41783 | 1.1097 | 55.4844 | 1.5506 | 9.7012 | 9.78 | 8.6651 | 9.1 | 196 | 18.3664 | 0.023299 | 200 | 196 | 195.5 | 1.1457 | 0.0078083 | 1.125 | 0.89365 | 0.029223 | 0.27258 | 1.0966 | 1.1549 | 1.1573 | 1.1243 | 0.10305 | 0 | 0.023059 | 87.7175 | 11.8978 | 0.31887 | 0.032617 | 0.010097 | 0.27258 | 0.056478 | 1.142 | 1.0812 | 1.0332 | 1.0354 | 0.97495 | 1.006 | 1.0414 | 0.11405 | 0.1126 | 0.1154 | 0.011802 | 0.015664 | 0.015664 | 1.1369 | 7.4624 | 1.5506 | 0.54905 | 2.7083 | 0.58676 | 0.49041 | 1.8934 | 0.39498 | 1.1339 | 15.5383 | 1.6005 | 1.0658 | 10.6426 | 1.1715 | 1.1193 | 10.6916 | 1.2181 | 1.1284 | 72.3116 | 1.3342 | 1.1256 | 68.7027 | 1.285 | 1.1265 | 68.1294 | 1.2756 | 392 | 0.20435 | 0.098864 | 0.05339 | 1.1169 | 0.02662 | 0.81298 | 0.15616 | 0.09285 | 0.42627 | 1.0173 | 1
Image_B200_ImageSize_128 | B_200 | 3600 | 1.3126 | 1.5049 | 0.41562 | 1.3126 | 1.1465 | 1.0564 | 86.0489 | 69.2308 | 112 | 1.4001 | 1.4457 | 0.42703 | 1.0187 | 50.934 | 1.4989 | 54.9415 | 60.06 | 9.5057 | 11.06 | 55 | 63.98 | 0.28196 | 88 | 52 | 52 | 1.0565 | 0.00054399 | 1.0333 | 0.79062 | 0.046609 | 0.15643 | 0.99736 | 1.0749 | 1.0828 | 1.031 | 0.15366 | 0 | 31.9189 | 60.8605 | 6.6043 | 0.24406 | 0.18916 | 0.18309 | 0.010244 | -0.016593 | 1.3508 | 1.4454 | 1.3519 | 1.3283 | 0.90169 | 0.89674 | 0.93419 | 0.089085 | 0.11165 | 0.11222 | 0.071356 | 0.10239 | 0.1024 | 1.0575 | 6.1457 | 1.3053 | 0.19786 | 1.102 | 0.2282 | 0.07302 | 0.52612 | 0.10523 | 1.0617 | 13.8736 | 1.4325 | 0.31141 | 3.3465 | 0.34893 | 0.073544 | 1.0624 | 0.10625 | 1.0619 | 83.7864 | 1.4341 | 0.92677 | 72.0899 | 1.2408 | 1.057 | 81.9588 | 1.4107 | 104 | 0.055063 | 0.15022 | 0.067692 | 0.97598 | 0.029047 | 0.77561 | 0.14659 | 0.076122 | 0.27754 | 1.3126 | 1
Image_B200_ModelSize_128 | B_200 | 3600 | 0.65184 | 1.2119 | 0.40032 | 0.65184 | 1.8592 | 0.79231 | 30.1867 | 11.3924 | 632 | 1.5165 | 1.1848 | 0.40683 | 0.77801 | 38.9003 | 1.2087 | 3.422 | 3.48 | 7.9642 | 8.78 | 316 | 11.3863 | 0.05211 | 316 | 316 | 0 | 0.80717 | 2.4154e-05 | 0.78943 | 0.41217 | 0.01155 | 0.11376 | 0.77468 | 0.80821 | 0.81004 | 0.78852 | 0.034987 | 0 | 0.047497 | 73.9386 | 25.4308 | 0.50986 | 0.058211 | 0.014977 | 0.066578 | -0.013138 | 0.72825 | 0.68413 | 0.66325 | 0.65814 | 0.70353 | 0.59361 | 0.6144 | 0.12439 | 0.099498 | 0.10146 | 0.015915 | 0.012465 | 0.012465 | 0.80481 | 3.7643 | 0.79091 | 0.57108 | 2.0831 | 0.45047 | 0.75805 | 2.5085 | 0.56343 | 0.8016 | 5.5168 | 0.61245 | 0.78966 | 5.1485 | 0.574 | 0.79101 | 5.3351 | 0.59449 | 0.79636 | 31.9816 | 0.59563 | 0.79131 | 30.9483 | 0.57618 | 0.79133 | 30.8123 | 0.57406 | 316 | 0.049924 | 0.033398 | 0.018919 | 0.64822 | 0.0032829 | 0.66222 | 0.12879 | 0.074954 | 0.35899 | 0.65184 | 1
Image_B200_ModelSize_256 | B_200 | 3600 | 0.73378 | 1.5493 | 0.40232 | 0.73378 | 2.1114 | 1.1258 | 27.96 | 21.9512 | 327 | 1.9052 | 1.5219 | 0.40851 | 1.1134 | 55.6676 | 1.5452 | 6.1114 | 6.18 | 15.8861 | 16.66 | 163 | 21.9975 | 0.065551 | 163.5 | 163.5 | 163.5 | 1.1425 | 0.0066566 | 1.1247 | 0.86476 | 0.029706 | 1.1119 | 1.1165 | 1.1408 | 1.1438 | 1.1237 | 0.092291 | 0 | 0.12012 | 89.9932 | 9.417 | 0.39017 | 0.055105 | 0.02448 | 1.1119 | 0.02535 | 0.87065 | 0.80393 | 0.7637 | 0.74497 | 0.98237 | 0.99383 | 1.0378 | 0.094192 | 0.091117 | 0.093371 | 0.0057959 | 0.0067237 | 0.0067237 | 1.1351 | 7.5339 | 1.5655 | 0.46098 | 2.2302 | 0.48194 | 0.14063 | 0.3515 | 0.071029 | 1.1354 | 12.6075 | 1.368 | 0.77243 | 6.6964 | 0.75545 | 1.1087 | 7.8685 | 0.92029 | 1.1312 | 52.0931 | 1.0247 | 1.1255 | 49.5518 | 0.97917 | 1.1249 | 49.9536 | 0.9886 | 324 | 0.82992 | 0.092088 | 0.051966 | 1.1091 | 0.015298 | 0.90121 | 0.34122 | 0.6007 | 0.54113 | 0.73378 | 1
Image_B200_ModelSize_512 | B_200 | 3600 | 0.75986 | 1.8138 | 0.40355 | 0.75986 | 2.387 | 1.3778 | 25.1356 | 56.25 | 135 | 1.7137 | 1.7702 | 0.40853 | 1.3616 | 68.0815 | 1.8023 | 13.4976 | 14.16 | 39.9618 | 43.362 | 67 | 53.2579 | 0.11186 | 67.5 | 67.5 | 64.5 | 1.3953 | 0.094901 | 1.373 | 1.3241 | 0.089062 | 1.2247 | 1.3273 | 1.3994 | 1.41 | 1.3724 | 0.13518 | 0 | 7.0407 | 85.9347 | 6.7707 | 0.19301 | 0.03806 | 0.022785 | 1.2247 | -0.0096941 | 0.95381 | 0.87788 | 0.84692 | 0.80324 | 1.1389 | 1.3858 | 1.4444 | 0.055452 | 0.061697 | 0.063258 | 0.00065072 | 0.00026617 | 0.00026617 | 1.3884 | 10.6654 | 2.2206 | 0.22664 | 1.3166 | 0.28367 | 0.0060536 | 0.012393 | 0.0024786 | 1.3895 | 22.3686 | 2.3001 | 0.43285 | 4.5984 | 0.51505 | 0.021629 | 0.10605 | 0.010799 | 1.3801 | 72.1639 | 1.4825 | 1.3777 | 62.8158 | 1.3125 | 1.377 | 60.9371 | 1.2797 | 132 | 0.91214 | 0.10863 | 0.038159 | 1.3693 | 0.049652 | 1.0018 | 0.48877 | 0.73059 | 0.5597 | 0.75986 | 1
Text_B200_BatchSize2 | B_200 | 3600 | 0.78157 | 0.88893 | 0.40656 | 0.78157 | 1.1374 | 0.43512 | 88.8667 | 17.3077 | 208 | 0.6297 | 0.82547 | 0.41558 | 0.40989 | 20.4945 | 0.87259 | 31.2322 | 34 | 3.5638 | 2.7 | 103 | 34.5527 | 0.15805 | 104 | 0 | 0 | 0.47323 | 2.5839e-10 | 0.4221 | 0.20102 | 0.071344 | 0.064825 | 0.40385 | 0.46036 | 0.47365 | 0.41601 | 0.24191 | 0 | 37.3093 | 34.0006 | 27.982 | 0.45967 | 0.20697 | 0.041462 | 0.02236 | 0.0039378 | 0.79035 | 0.81597 | 0.80335 | 0.80346 | 0.35729 | 0.21832 | 0.22225 | 0.038212 | 0.027219 | 0.02732 | 0.019754 | 0.016234 | 0.016235 | 0.44575 | 1.6279 | 0.333 | 0.11071 | 0.39713 | 0.080771 | 0.043958 | 0.18118 | 0.036241 | 0.43981 | 3.444 | 0.3485 | 0.17286 | 1.2943 | 0.13135 | 0.052395 | 0.43052 | 0.043059 | 0.42509 | 16.3595 | 0.27473 | 0.29627 | 13.7409 | 0.23145 | 0.32529 | 15.4476 | 0.25931 | 0 | 0.025059 | 0.22365 | 0.077781 | 0.25383 | 0.052508 | 0.41581 | 0.085996 | 0.052317 | 0.13852 | 0.78157 | 1
Text_B200_BatchSize16 | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949 | 1.7278 | 0.44897 | 1.2789 | 63.9437 | 1.8632 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 404 | 400 | 396 | 1.452 | 0.28179 | 1.3641 | 1.1783 | 0.26927 | 0.23807 | 1.4131 | 1.4407 | 1.4479 | 1.3619 | 1.0437 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 2.373e-05 | 0.034995 | 1.4758 | 1.4894 | 1.4717 | 1.4704 | 1.2692 | 1.491 | 1.5639 | 0.28993 | 0.34461 | 0.35356 | 0.11194 | 0.17089 | 0.17256 | 1.427 | 10.4133 | 2.1895 | 0.95265 | 6.6213 | 1.3901 | 1.3063 | 8.3257 | 1.7679 | 1.4044 | 21.2091 | 2.1983 | 1.2586 | 18.3784 | 1.9143 | 1.3432 | 19.7977 | 2.0498 | 1.3752 | 121.9861 | 2.1156 | 1.2787 | 111.6169 | 1.9384 | 1.3599 | 119.1032 | 2.0711 | 396 | 0.099207 | 1.0246 | 0.34813 | 1.3189 | 0.20744 | 1.483 | 0.33901 | 0.15368 | 0.69438 | 1.3932 | 1
Text_B200_BatchSize32 | B_200 | 3600 | 1.5345 | 1.9612 | 0.41814 | 1.5345 | 1.2781 | 1.4353 | 81.3444 | 9.0909 | 808 | 3.492 | 1.8023 | 0.51502 | 1.2873 | 64.3644 | 1.9438 | 7.2608 | 7.54 | 1.6564 | 1.9 | 403 | 8.9104 | 0.076621 | 800 | 404 | 399.5 | 1.4803 | 0.74913 | 1.3336 | 0.41961 | 0.015152 | 0.27708 | 1.4725 | 1.5175 | 1.5183 | 1.2976 | 0.046048 | 0 | 0.15471 | 1.1689 | 97.1631 | 0.98678 | 0.44353 | 0.082978 | 0.17545 | 0.00078126 | 1.5984 | 1.5825 | 1.5516 | 1.5448 | 1.2739 | 1.6677 | 1.7418 | 0.37121 | 0.48323 | 0.49534 | 0.28747 | 0.31077 | 0.32568 | 1.4851 | 11.7657 | 2.4408 | 1.0538 | 7.6878 | 1.6157 | 1.3875 | 9.1944 | 1.9694 | 1.4813 | 23.3079 | 2.4228 | 1.423 | 21.8344 | 2.274 | 1.4263 | 21.8981 | 2.2708 | 1.4512 | 134.7761 | 2.3371 | 1.4362 | 132.224 | 2.2955 | 1.4368 | 132.1934 | 2.2943 | 417 | 0.14467 | 0.04352 | 0.025143 | 0.64199 | 0.011699 | 1.6019 | 0.48432 | 0.20738 | 0.75936 | 1.5345 | 1
Text_B200_Deepspeedds_z1 | B_200 | 3600 | 1.3283 | 2 | 0.40753 | 1.3283 | 1.5057 | 1.4992 | 70.1844 | 7.9646 | 824 | 3.7532 | 1.7124 | 0.44076 | 1.2716 | 63.5803 | 1.9834 | 6.1758 | 6.4 | 2.5715 | 2 | 411 | 8.7335 | 0.9838 | 648 | 412 | 411.5 | 1.5056 | 0.87763 | 1.4238 | 1.1835 | 0.37444 | 0.60244 | 1.5252 | 1.5597 | 1.5687 | 1.3927 | 0.92206 | 0 | 29.0813 | 2.784 | 62.0211 | 5.59 | 0.43961 | 0.08395 | 0.59802 | 0.081701 | 1.431 | 1.4701 | 1.4443 | 1.4362 | 1.3595 | 1.727 | 1.8014 | 0.40709 | 0.52891 | 0.5415 | 0.31371 | 0.4753 | 0.47816 | 1.5196 | 11.8371 | 2.4584 | 1.1139 | 7.6479 | 1.6149 | 1.4347 | 9.0609 | 1.9384 | 1.5065 | 23.0756 | 2.3944 | 1.3444 | 19.0486 | 2.0051 | 1.4745 | 20.8606 | 2.1968 | 1.4921 | 129.3674 | 2.2654 | 1.4601 | 117.3759 | 2.0762 | 1.4803 | 126.4283 | 2.2171 | 5 | 0.44888 | 0.89333 | 0.27895 | 1.3299 | 0.28973 | 1.6774 | 0.63759 | 0.31233 | 0.79763 | 1.3283 | 1
Text_B200_Deepspeedds_z2 | B_200 | 3600 | 1.3723 | 1.887 | 0.41212 | 1.3723 | 1.3751 | 1.3605 | 74.5778 | 8.5714 | 815 | 3.0408 | 1.714 | 0.44392 | 1.2701 | 63.5059 | 1.8631 | 6.6051 | 6.9 | 2.1171 | 1.94 | 407 | 8.707 | 0.48509 | 415.5 | 407.5 | 396 | 1.4493 | 0.30285 | 1.3431 | 0.99899 | 0.22489 | 0.99439 | 1.3919 | 1.4448 | 1.4457 | 1.3407 | 0.83994 | 0 | 19.7537 | 2.5003 | 76.5089 | 0.77496 | 0.38857 | 0.073518 | 0.9943 | 0.032995 | 1.4565 | 1.4497 | 1.4443 | 1.4395 | 1.2118 | 1.4641 | 1.517 | 0.2956 | 0.34569 | 0.35482 | 0.13073 | 0.18442 | 0.18446 | 1.4251 | 10.343 | 2.1622 | 0.98144 | 6.6382 | 1.4007 | 1.2975 | 8.0329 | 1.7188 | 1.4141 | 21.083 | 2.1871 | 1.2807 | 18.207 | 1.9059 | 1.3448 | 19.3385 | 2.0169 | 1.3701 | 118.4675 | 2.0651 | 1.3502 | 111.2722 | 1.9515 | 1.3496 | 115.6842 | 2.0175 | 404 | 0.74163 | 0.82635 | 0.28124 | 1.3017 | 0.1572 | 1.4889 | 0.40617 | 0.56547 | 0.73709 | 1.3723 | 1
Text_B200_Deepspeedds_z3 | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949 | 1.7278 | 0.44897 | 1.2789 | 63.9437 | 1.8632 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 404 | 400 | 396 | 1.452 | 0.28179 | 1.3641 | 1.1783 | 0.26927 | 0.23807 | 1.4131 | 1.4407 | 1.4479 | 1.3619 | 1.0437 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 2.373e-05 | 0.034995 | 1.4758 | 1.4894 | 1.4717 | 1.4704 | 1.2692 | 1.491 | 1.5639 | 0.28993 | 0.34461 | 0.35356 | 0.11194 | 0.17089 | 0.17256 | 1.427 | 10.4133 | 2.1895 | 0.95265 | 6.6213 | 1.3901 | 1.3063 | 8.3257 | 1.7679 | 1.4044 | 21.2091 | 2.1983 | 1.2586 | 18.3784 | 1.9143 | 1.3432 | 19.7977 | 2.0498 | 1.3752 | 121.9861 | 2.1156 | 1.2787 | 111.6169 | 1.9384 | 1.3599 | 119.1032 | 2.0711 | 396 | 0.099207 | 1.0246 | 0.34813 | 1.3189 | 0.20744 | 1.483 | 0.33901 | 0.15368 | 0.69438 | 1.3932 | 1
Text_B200_Lamma_1B | B_200 | 3600 | 0.82231 | 1.3127 | 0.40789 | 0.82231 | 1.5964 | 0.85262 | 48.12 | 4.4776 | 1599 | 2.3255 | 1.2043 | 0.43361 | 0.77068 | 38.5342 | 1.2993 | 2.171 | 2.28 | 2.3326 | 2.522 | 799 | 4.5037 | 0.15552 | 799.5 | 792 | 0 | 0.87897 | 0.0001482 | 0.82381 | 0.19878 | 0.016759 | 0.60963 | 0.85323 | 0.89746 | 0.89762 | 0.81808 | 0.064544 | 0 | 0.4565 | 1.1689 | 97.0705 | 0.59672 | 0.59764 | 0.10968 | 0.60963 | -0.008328 | 0.88475 | 0.84464 | 0.83481 | 0.82918 | 0.75827 | 0.67265 | 0.69452 | 0.33033 | 0.27661 | 0.28202 | 0.31881 | 0.27139 | 0.27718 | 0.88335 | 3.9515 | 0.84571 | 0.83758 | 3.4597 | 0.74312 | 0.84981 | 3.4692 | 0.74713 | 0.87458 | 7.6907 | 0.82208 | 0.84904 | 6.9839 | 0.75062 | 0.85011 | 6.9581 | 0.74729 | 0.85825 | 42.8502 | 0.76731 | 0.85185 | 42.0296 | 0.7536 | 0.85418 | 42.3604 | 0.75816 | 5 | 0.45858 | 0.059693 | 0.023626 | 0.12315 | 0.0066373 | 0.99762 | 0.24802 | 0.34082 | 0.48625 | 0.82231 | 1
Text_B200_Lamma_3B | B_200 | 3600 | 1.0446 | 1.6056 | 0.40919 | 1.0446 | 1.5371 | 1.1156 | 56.9089 | 6.8702 | 1039 | 2.5454 | 1.4823 | 0.42658 | 1.0557 | 52.7862 | 1.5852 | 4.2316 | 4.4 | 2.6954 | 2.7 | 519 | 6.9269 | 0.37202 | 520 | 515.5 | 515.5 | 1.1668 | 0.014885 | 1.1 | 0.40183 | 0.091413 | 0.57405 | 1.11 | 1.1917 | 1.1962 | 1.1003 | 0.3131 | 0 | 4.9876 | 1.7824 | 91.691 | 1.0999 | 0.38827 | 0.050956 | 0.5572 | 0.022894 | 1.1361 | 1.0931 | 1.0842 | 1.0807 | 0.98026 | 1.0225 | 1.0584 | 0.29133 | 0.28971 | 0.29606 | 0.27344 | 0.2349 | 0.24168 | 1.1611 | 7.108 | 1.4747 | 1.0456 | 5.5454 | 1.1949 | 1.0988 | 5.5792 | 1.2097 | 1.1536 | 13.6003 | 1.4408 | 1.0753 | 11.4538 | 1.2359 | 1.1118 | 11.7322 | 1.2728 | 1.1236 | 72.3215 | 1.3008 | 1.1133 | 69.8001 | 1.263 | 1.1138 | 70.9342 | 1.2804 | 5 | 0.41313 | 0.29962 | 0.10871 | 0.64633 | 0.071405 | 1.4613 | 0.22979 | 0.29859 | 0.56302 | 1.0446 | 1
Text_B200_Lamma_8B | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949 | 1.7278 | 0.44897 | 1.2789 | 63.9437 | 1.8632 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 404 | 400 | 396 | 1.452 | 0.28179 | 1.3641 | 1.1783 | 0.26927 | 0.23807 | 1.4131 | 1.4407 | 1.4479 | 1.3619 | 1.0437 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 2.373e-05 | 0.034995 | 1.4758 | 1.4894 | 1.4717 | 1.4704 | 1.2692 | 1.491 | 1.5639 | 0.28993 | 0.34461 | 0.35356 | 0.11194 | 0.17089 | 0.17256 | 1.427 | 10.4133 | 2.1895 | 0.95265 | 6.6213 | 1.3901 | 1.3063 | 8.3257 | 1.7679 | 1.4044 | 21.2091 | 2.1983 | 1.2586 | 18.3784 | 1.9143 | 1.3432 | 19.7977 | 2.0498 | 1.3752 | 121.9861 | 2.1156 | 1.2787 | 111.6169 | 1.9384 | 1.3599 | 119.1032 | 2.0711 | 396 | 0.099207 | 1.0246 | 0.34813 | 1.3189 | 0.20744 | 1.483 | 0.33901 | 0.15368 | 0.69438 | 1.3932 | 1
Text_B200_SeqLength_1024 | B_200 | 3600 | 1.3928 | 1.8798 | 0.4125 | 1.3928 | 1.3497 | 1.3656 | 75.46 | 8.7379 | 792 | 3.1259 | 1.7269 | 0.44838 | 1.2785 | 63.9268 | 1.8636 | 6.8683 | 7.03 | 2.1257 | 2.04 | 396 | 8.994 | 0.3737 | 408 | 396 | 396 | 1.441 | 0.36164 | 1.3304 | 0.50101 | 0.18038 | 0.23982 | 1.4014 | 1.4428 | 1.4494 | 1.3233 | 0.65369 | 0 | 15.1867 | 2.5589 | 80.8655 | 0.9394 | 0.38934 | 0.06008 | 0.0075898 | 0.024434 | 1.4745 | 1.4635 | 1.4523 | 1.4463 | 1.2663 | 1.4989 | 1.5625 | 0.2959 | 0.34878 | 0.35793 | 0.12746 | 0.18394 | 0.18507 | 1.413 | 10.5406 | 2.1877 | 1.0008 | 6.7997 | 1.4356 | 1.3104 | 8.0961 | 1.7334 | 1.407 | 21.3716 | 2.2193 | 1.3076 | 18.7077 | 1.9597 | 1.3555 | 19.6456 | 2.0548 | 1.3764 | 119.2862 | 2.0866 | 1.3611 | 113.8063 | 1.9992 | 1.3625 | 117.0651 | 2.0431 | 396 | 0.10254 | 0.6382 | 0.21761 | 0.76309 | 0.12666 | 1.4661 | 0.33302 | 0.15859 | 0.68406 | 1.3928 | 1
Text_B200_SeqLength_2048 | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949 | 1.7278 | 0.44897 | 1.2789 | 63.9437 | 1.8632 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 404 | 400 | 396 | 1.452 | 0.28179 | 1.3641 | 1.1783 | 0.26927 | 0.23807 | 1.4131 | 1.4407 | 1.4479 | 1.3619 | 1.0437 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 2.373e-05 | 0.034995 | 1.4758 | 1.4894 | 1.4717 | 1.4704 | 1.2692 | 1.491 | 1.5639 | 0.28993 | 0.34461 | 0.35356 | 0.11194 | 0.17089 | 0.17256 | 1.427 | 10.4133 | 2.1895 | 0.95265 | 6.6213 | 1.3901 | 1.3063 | 8.3257 | 1.7679 | 1.4044 | 21.2091 | 2.1983 | 1.2586 | 18.3784 | 1.9143 | 1.3432 | 19.7977 | 2.0498 | 1.3752 | 121.9861 | 2.1156 | 1.2787 | 111.6169 | 1.9384 | 1.3599 | 119.1032 | 2.0711 | 396 | 0.099207 | 1.0246 | 0.34813 | 1.3189 | 0.20744 | 1.483 | 0.33901 | 0.15368 | 0.69438 | 1.3932 | 1
Text_B200_SeqLength_4096 | B_200 | 3600 | 1.394 | 1.8821 | 0.41118 | 1.394 | 1.3502 | 1.3675 | 75.2956 | 8.6538 | 792 | 3.1524 | 1.7277 | 0.44861 | 1.2791 | 63.953 | 1.8649 | 6.8543 | 6.985 | 2.1246 | 2.08 | 396 | 8.9789 | 0.43277 | 411.5 | 396.5 | 396 | 1.4345 | 0.34418 | 1.3355 | 0.59371 | 0.19904 | 0.8162 | 1.407 | 1.4379 | 1.4417 | 1.3297 | 0.73035 | 0 | 17.8616 | 2.5654 | 78.1502 | 0.98671 | 0.36748 | 0.068649 | 0.8162 | 0.035312 | 1.4761 | 1.4664 | 1.4541 | 1.4531 | 1.2208 | 1.4823 | 1.5313 | 0.29363 | 0.34498 | 0.35405 | 0.11691 | 0.1745 | 0.17456 | 1.4165 | 10.4936 | 2.1844 | 0.9734 | 6.6262 | 1.3985 | 1.3125 | 8.2021 | 1.7552 | 1.406 | 21.199 | 2.1975 | 1.2983 | 18.6655 | 1.9543 | 1.3569 | 19.6463 | 2.0501 | 1.377 | 120.144 | 2.0963 | 1.3624 | 114.0092 | 2.001 | 1.3628 | 117.2046 | 2.0457 | 400 | 0.60679 | 0.72367 | 0.2461 | 0.75657 | 0.13453 | 1.5104 | 0.38043 | 0.51021 | 0.72039 | 1.394 | 1

## Electrical_characteristics
scenario | I_IGBT_rms_A | I_IGBT_peak_A | I_Diode_rms_A | I_Diode_peak_A | P_loss_IGBT_mean_W | P_loss_IGBT_max_W | P_loss_IGBT_swing_W | P_loss_Diode_mean_W | P_loss_Diode_max_W | P_loss_Diode_swing_W | Switching_share_pct | Diode_share_pct | Loss_ratio_pct
Image_B200_BatchSize_128 | 335.2774 | 1183.4912 | 99.3998 | 274.7918 | 276.8739 | 532.2978 | 359.2093 | 23.1663 | 44.0523 | 29.4277 | 49.7794 | 7.7211 | 0.04603
Image_B200_BatchSize_256 | 342 | 1362.2452 | 101.3928 | 316.2962 | 276.5825 | 621.9714 | 441.2811 | 23.1181 | 51.2252 | 35.9993 | 49.6284 | 7.7137 | 0.04617
Image_B200_BatchSize_512 | 346.9532 | 1474.0627 | 102.8613 | 342.2588 | 278.3131 | 679.3034 | 501.0699 | 23.2491 | 55.7814 | 40.756 | 49.5424 | 7.7095 | 0.04625
Image_B200_ImageSize_128 | 621.8799 | 1469.6426 | 184.3689 | 341.2325 | 585.0244 | 677.019 | 490.6549 | 48.1884 | 55.6003 | 39.892 | 47.4976 | 7.6101 | 0.048241
Image_B200_ImageSize_32 | 335.2774 | 1183.4912 | 99.3998 | 274.7918 | 276.8739 | 532.2978 | 359.2093 | 23.1663 | 44.0523 | 29.4277 | 49.7794 | 7.7211 | 0.04603
Image_B200_ImageSize_64 | 525.7733 | 1532.7628 | 155.8762 | 355.8882 | 449.4157 | 709.7818 | 524.9165 | 37.1237 | 58.1946 | 42.6288 | 47.9091 | 7.6301 | 0.047827
Image_B200_ModelSize_128 | 335.2774 | 1183.4912 | 99.3998 | 274.7918 | 276.8739 | 532.2978 | 359.2093 | 23.1663 | 44.0523 | 29.4277 | 49.7794 | 7.7211 | 0.04603
Image_B200_ModelSize_256 | 400.8373 | 1512.9948 | 118.8363 | 351.2983 | 317.5277 | 699.4885 | 524.1709 | 26.4059 | 57.3802 | 42.585 | 48.8854 | 7.6776 | 0.046872
Image_B200_ModelSize_512 | 439.1247 | 1771.2967 | 130.1874 | 411.2728 | 333.349 | 836.3348 | 653.9763 | 27.5984 | 68.1519 | 52.8156 | 48.2371 | 7.6461 | 0.047502
Image_H100_BatchSize_128 | 237.0244 | 844.7903 | 70.2707 | 196.1497 | 186.7893 | 369.0614 | 255.0061 | 15.7291 | 30.835 | 21.1708 | 50.7192 | 7.7668 | 0.045177
Image_H100_BatchSize_256 | 216.1582 | 638.6349 | 64.0845 | 148.283 | 178.8793 | 273.9837 | 167.9054 | 15.0991 | 23.0295 | 14.0135 | 51.0723 | 7.7839 | 0.044865
Image_H100_BatchSize_512 | 246.2676 | 1100.4691 | 73.011 | 255.5151 | 189.2689 | 491.4769 | 378.7234 | 15.9189 | 40.7672 | 31.217 | 50.5436 | 7.7582 | 0.045334
Image_H100_ImageSize_16 | 179.4119 | 581.6134 | 53.1903 | 135.0433 | 149.3872 | 248.2574 | 139.7113 | 12.6446 | 20.9026 | 11.6797 | 51.4803 | 7.8038 | 0.044509
Image_H100_ImageSize_32 | 237.0244 | 844.7903 | 70.2707 | 196.1497 | 186.7893 | 369.0614 | 255.0061 | 15.7291 | 30.835 | 21.1708 | 50.7192 | 7.7668 | 0.045177
Image_H100_ImageSize_64 | 431.4624 | 1159.554 | 127.9158 | 269.2338 | 365.4195 | 520.4743 | 408.9504 | 30.3822 | 43.1021 | 33.6482 | 48.8546 | 7.6761 | 0.046901
Image_H100_ModelSize_128 | 237.0244 | 844.7903 | 70.2707 | 196.1497 | 186.7893 | 369.0614 | 255.0061 | 15.7291 | 30.835 | 21.1708 | 50.7192 | 7.7668 | 0.045177
Image_H100_ModelSize_256 | 308.7807 | 1120.0008 | 91.5443 | 260.0501 | 231.6484 | 501.0331 | 389.8975 | 19.3756 | 41.5374 | 32.1167 | 49.7294 | 7.7186 | 0.046076
Image_H100_ModelSize_512 | 333.8535 | 1317.3611 | 98.9776 | 305.8747 | 239.5844 | 599.226 | 476.6221 | 19.9739 | 49.4113 | 39.082 | 49.2501 | 7.6953 | 0.046525
Text_B200_BatchSize16 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906
Text_B200_BatchSize2 | 363.8699 | 868.0945 | 107.8766 | 201.5606 | 331.5703 | 380.0128 | 191.981 | 27.7541 | 31.7287 | 15.865 | 49.8391 | 7.724 | 0.045975
Text_B200_BatchSize32 | 735.9011 | 1915.2764 | 218.1728 | 444.7031 | 699.2431 | 914.8205 | 688.9342 | 57.192 | 74.2796 | 55.4482 | 46.4812 | 7.5607 | 0.049296
Text_B200_Deepspeedds_z1 | 658.807 | 1953.1287 | 195.3167 | 453.4919 | 599.3242 | 935.7165 | 719.5298 | 49.1733 | 75.9053 | 57.9123 | 46.9319 | 7.5826 | 0.048823
Text_B200_Deepspeedds_z2 | 670.5766 | 1842.7441 | 198.8061 | 427.862 | 619.3966 | 875.0846 | 647.762 | 50.8145 | 71.1816 | 52.2643 | 46.9159 | 7.5819 | 0.048839
Text_B200_Deepspeedds_z3 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906
Text_B200_Lamma_1B | 407.3297 | 1281.9597 | 120.7612 | 297.6549 | 353.4174 | 581.3943 | 389.0648 | 29.4564 | 47.9867 | 31.8083 | 49.2121 | 7.6935 | 0.046561
Text_B200_Lamma_3B | 523.0716 | 1568.0157 | 155.0752 | 364.0735 | 459.733 | 728.2121 | 520.2929 | 38.0228 | 59.6509 | 42.2472 | 48.0879 | 7.6388 | 0.047649
Text_B200_Lamma_8B | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906
Text_B200_SeqLength_1024 | 678.8393 | 1835.7063 | 201.2557 | 426.2279 | 629.4087 | 871.2503 | 651.0014 | 51.6161 | 70.8822 | 52.5049 | 46.8606 | 7.5792 | 0.048897
Text_B200_SeqLength_2048 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906
Text_B200_SeqLength_4096 | 679.5989 | 1837.9769 | 201.4809 | 426.7551 | 630.0543 | 872.4869 | 651.9624 | 51.6662 | 70.9788 | 52.5811 | 46.8527 | 7.5788 | 0.048905
Text_H100_BatchSize16 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473
Text_H100_BatchSize2 | 260.401 | 640.6399 | 77.2012 | 148.7485 | 231.9003 | 274.8928 | 154.2087 | 19.5377 | 23.1046 | 12.8781 | 50.7938 | 7.7704 | 0.045111
Text_H100_BatchSize32 | 549.2604 | 1398.1791 | 162.8394 | 324.6396 | 507.5329 | 640.2919 | 500.3092 | 41.978 | 52.6836 | 40.9403 | 48.0943 | 7.6392 | 0.047643
Text_H100_Deepspeedds_z1 | 506.9762 | 1439.7841 | 150.3034 | 334.2997 | 450.658 | 661.6265 | 540.0433 | 37.3292 | 54.379 | 44.1207 | 48.3099 | 7.6496 | 0.04743
Text_H100_Deepspeedds_z2 | 514.6392 | 1363.7084 | 152.5752 | 316.6359 | 469.8086 | 622.7155 | 472.7041 | 38.9313 | 51.2845 | 38.7437 | 48.3688 | 7.6525 | 0.047372
Text_H100_Deepspeedds_z3 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473
Text_H100_Lamma_1B | 352.4445 | 1145.0086 | 104.4893 | 265.8566 | 294.3917 | 513.3111 | 384.1786 | 24.6081 | 42.526 | 31.653 | 49.6369 | 7.7141 | 0.046162
Text_H100_Lamma_3B | 454.7773 | 1286.4983 | 134.828 | 298.7087 | 397.7909 | 583.6751 | 447.2455 | 33.0524 | 48.1691 | 36.7157 | 48.7608 | 7.6716 | 0.046992
Text_H100_Lamma_8B | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473
Text_H100_SeqLength_1024 | 527.0567 | 1371.6325 | 156.2567 | 318.4758 | 483.4427 | 626.748 | 480.1819 | 40.0343 | 51.6056 | 39.3389 | 48.2716 | 7.6478 | 0.047468
Text_H100_SeqLength_2048 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473
Text_H100_SeqLength_4096 | 526.2989 | 1369.2247 | 156.032 | 317.9167 | 482.2831 | 625.5221 | 480.3823 | 39.939 | 51.508 | 39.3557 | 48.2741 | 7.6479 | 0.047465

## Thermal_characteristics
scenario | Tj_IGBT_mean_C | Tj_IGBT_max_C | Tj_IGBT_min_C | Tj_IGBT_swing_K | Tj_Diode_mean_C | Tj_Diode_max_C | Tj_Diode_min_C | Tj_Diode_swing_K | T_case_mean_C | T_case_swing_K | IGBT_cycles_per_h | IGBT_dT_max_K | IGBT_dT_mean_K | IGBT_dT_p95_K | IGBT_cycles_dT_lt5_per_h | IGBT_cycles_dT_5_10_per_h | IGBT_cycles_dT_10_20_per_h | IGBT_cycles_dT_ge20_per_h | IGBT_cycle_Tmean_C | IGBT_cycle_duration_mean_s | IGBT_cycle_duration_p95_s | IGBT_grid_cycles_per_h | IGBT_grid_cycle_dT_mean_K | IGBT_grid_cycle_dT_max_K | IGBT_load_cycles_per_h | IGBT_load_cycle_dT_mean_K | IGBT_load_cycle_dT_max_K | IGBT_load_cycle_Tmean_C | IGBT_load_cycle_duration_mean_s | IGBT_burst_cycles_per_h | IGBT_burst_dT_mean_K | IGBT_burst_dT_median_K | IGBT_burst_dT_p95_K | IGBT_burst_dT_max_K | IGBT_burst_dT_eq_K | IGBT_burst_Tmean_C | IGBT_burst_duration_mean_s | Diode_cycles_per_h | Diode_dT_max_K | Diode_dT_mean_K | Diode_dT_p95_K | Diode_cycles_dT_lt5_per_h | Diode_cycles_dT_5_10_per_h | Diode_cycles_dT_10_20_per_h | Diode_cycles_dT_ge20_per_h | Diode_cycle_Tmean_C | Diode_cycle_duration_mean_s | Diode_cycle_duration_p95_s | Diode_grid_cycles_per_h | Diode_grid_cycle_dT_mean_K | Diode_grid_cycle_dT_max_K | Diode_load_cycles_per_h | Diode_load_cycle_dT_mean_K | Diode_load_cycle_dT_max_K | Diode_load_cycle_Tmean_C | Diode_load_cycle_duration_mean_s | Diode_burst_cycles_per_h | Diode_burst_dT_mean_K | Diode_burst_dT_median_K | Diode_burst_dT_p95_K | Diode_burst_dT_max_K | Diode_burst_dT_eq_K | Diode_burst_Tmean_C | Diode_burst_duration_mean_s
Image_B200_BatchSize_128 | 104.1579 | 111.6634 | 25 | 22.08 | 100.1673 | 103.7059 | 25 | 18.4027 | 99.2618 | 17.6995 | 180000.0417 | 86.6634 | 0.59269 | 1.1252 | 179684.0417 | 315.9583 | 0 | 0.041667 | 104.1731 | 0.048354 | 0.013 | 179107.6667 | 0.58133 | 1.1416 | 892.375 | 2.8738 | 86.6634 | 105.0413 | 7.8042 | 315.9583 | 6.8358 | 6.8466 | 6.9442 | 6.9997 | 6.8408 | 105.5222 | 15.8301 | 180000 | 78.7059 | 0.1287 | 0.24116 | 179999.9583 | 0 | 0 | 0.041667 | 100.1682 | 0.043098 | 0.012 | 179219.9583 | 0.12673 | 0.24424 | 780.0417 | 0.58059 | 78.7059 | 100.3419 | 7.6771 | 0
Image_B200_BatchSize_256 | 104.0692 | 113.0589 | 25 | 23.2855 | 100.0819 | 103.8657 | 25 | 18.5833 | 99.1783 | 17.7142 | 180000.0417 | 88.0589 | 0.59226 | 1.3012 | 179676.0833 | 323.9167 | 0 | 0.041667 | 104.0844 | 0.049375 | 0.013 | 179132.5 | 0.57848 | 1.3203 | 867.5417 | 3.4371 | 88.0589 | 104.2064 | 8.2549 | 323.9167 | 8.2764 | 8.2886 | 8.3586 | 8.4719 | 8.2806 | 106.172 | 16.0183 | 180003.9167 | 78.8657 | 0.12844 | 0.27753 | 180003.875 | 0 | 0 | 0.041667 | 100.0828 | 0.048495 | 0.012 | 179032.7083 | 0.12603 | 0.2813 | 971.2083 | 0.57332 | 78.8657 | 100.3111 | 7.1541 | 0
Image_B200_BatchSize_512 | 104.5599 | 114.6089 | 25 | 24.1752 | 100.5471 | 104.5578 | 25 | 18.8618 | 99.6383 | 17.8366 | 180000.0417 | 89.6089 | 0.59606 | 1.4278 | 179672.0417 | 327.9583 | 0 | 0.041667 | 104.5752 | 0.048292 | 0.013 | 178836.7917 | 0.57996 | 1.457 | 1163.25 | 3.0712 | 89.6089 | 104.5447 | 6.0244 | 327.9583 | 9.358 | 9.3581 | 9.4746 | 9.5398 | 9.3615 | 107.167 | 14.8263 | 180000 | 79.5578 | 0.12918 | 0.30362 | 179999.9583 | 0 | 0 | 0.041667 | 100.5479 | 0.04704 | 0.012 | 178806.5 | 0.12635 | 0.309 | 1193.5 | 0.55349 | 79.5578 | 100.4873 | 5.6321 | 0
Image_B200_ImageSize_128 | 192.0737 | 200.1238 | 25 | 39.2307 | 183.6118 | 189.9394 | 25 | 37.7968 | 181.7284 | 37.4004 | 180000.0417 | 175.1238 | 1.2581 | 1.4199 | 179948 | 52 | 0 | 0.041667 | 192.1085 | 0.051728 | 0.013 | 174731.4583 | 1.2437 | 1.4376 | 5268.5833 | 1.7348 | 175.1238 | 192.6605 | 1.4367 | 52 | 9.5748 | 9.5859 | 9.9498 | 9.9527 | 9.5946 | 189.6476 | 53.5986 | 180000 | 164.9394 | 0.2681 | 0.30255 | 179999.9583 | 0 | 0 | 0.041667 | 183.6139 | 0.050208 | 0.012 | 174253.4167 | 0.26534 | 0.3062 | 5746.5833 | 0.35164 | 164.9394 | 183.5115 | 1.2612 | 0
Image_B200_ImageSize_32 | 104.1579 | 111.6634 | 25 | 22.08 | 100.1673 | 103.7059 | 25 | 18.4027 | 99.2618 | 17.6995 | 180000.0417 | 86.6634 | 0.59269 | 1.1252 | 179684.0417 | 315.9583 | 0 | 0.041667 | 104.1731 | 0.048354 | 0.013 | 179107.6667 | 0.58133 | 1.1416 | 892.375 | 2.8738 | 86.6634 | 105.0413 | 7.8042 | 315.9583 | 6.8358 | 6.8466 | 6.9442 | 6.9997 | 6.8408 | 105.5222 | 15.8301 | 180000 | 78.7059 | 0.1287 | 0.24116 | 179999.9583 | 0 | 0 | 0.041667 | 100.1682 | 0.043098 | 0.012 | 179219.9583 | 0.12673 | 0.24424 | 780.0417 | 0.58059 | 78.7059 | 100.3419 | 7.6771 | 0
Image_B200_ImageSize_64 | 153.3771 | 162.8751 | 25 | 33.5339 | 146.8808 | 152.2169 | 25 | 29.4039 | 145.4297 | 28.7241 | 180000.0417 | 137.8751 | 0.96566 | 1.4945 | 179804.0417 | 46.1667 | 149.7917 | 0.041667 | 153.4034 | 0.044335 | 0.013 | 178306.7083 | 0.95283 | 1.5121 | 1693.3333 | 2.3162 | 137.8751 | 156.1296 | 3.5859 | 195.9583 | 10.0307 | 10.0325 | 10.1517 | 10.3747 | 10.0373 | 153.4522 | 19.4442 | 180000 | 127.2169 | 0.20648 | 0.31663 | 179999.9583 | 0 | 0 | 0.041667 | 146.8823 | 0.04291 | 0.012 | 179081.5 | 0.20465 | 0.3203 | 918.5 | 0.56329 | 127.2169 | 147.9603 | 6.3342 | 0
Image_B200_ModelSize_128 | 104.1579 | 111.6634 | 25 | 22.08 | 100.1673 | 103.7059 | 25 | 18.4027 | 99.2618 | 17.6995 | 180000.0417 | 86.6634 | 0.59269 | 1.1252 | 179684.0417 | 315.9583 | 0 | 0.041667 | 104.1731 | 0.048354 | 0.013 | 179107.6667 | 0.58133 | 1.1416 | 892.375 | 2.8738 | 86.6634 | 105.0413 | 7.8042 | 315.9583 | 6.8358 | 6.8466 | 6.9442 | 6.9997 | 6.8408 | 105.5222 | 15.8301 | 180000 | 78.7059 | 0.1287 | 0.24116 | 179999.9583 | 0 | 0 | 0.041667 | 100.1682 | 0.043098 | 0.012 | 179219.9583 | 0.12673 | 0.24424 | 780.0417 | 0.58059 | 78.7059 | 100.3419 | 7.6771 | 0
Image_B200_ModelSize_256 | 115.738 | 126.1956 | 25 | 27.0192 | 111.1552 | 115.6196 | 25 | 21.3546 | 110.123 | 20.4615 | 180000.0417 | 101.1956 | 0.68095 | 1.4848 | 179836.0833 | 30.7917 | 133.125 | 0.041667 | 115.756 | 0.051685 | 0.013 | 178969.1667 | 0.67098 | 1.5159 | 1030.875 | 2.4122 | 101.1956 | 117.415 | 7.3931 | 163.9167 | 10.0619 | 10.0869 | 10.2081 | 10.3676 | 10.0716 | 117.9524 | 33.5052 | 180003.9167 | 90.6196 | 0.14678 | 0.31459 | 180003.875 | 0 | 0 | 0.041667 | 111.1562 | 0.051824 | 0.012 | 179275.875 | 0.1452 | 0.31939 | 728.0417 | 0.53405 | 90.6196 | 110.9796 | 10.4356 | 0
Image_B200_ModelSize_512 | 120.2227 | 133.46 | 25 | 30.286 | 115.4067 | 120.9244 | 25 | 22.9478 | 114.3279 | 22.0264 | 180000.0417 | 108.46 | 0.7158 | 1.7617 | 179932.0417 | 4 | 63.9583 | 0.041667 | 120.2421 | 0.042085 | 0.013 | 177000.5417 | 0.69492 | 1.8307 | 2999.5 | 1.9478 | 108.46 | 127.1044 | 2.0366 | 67.9583 | 13.0285 | 13.3441 | 13.8176 | 13.9665 | 13.3143 | 123.2649 | 54.618 | 180000 | 95.9244 | 0.15347 | 0.37062 | 179999.9583 | 0 | 0 | 0.041667 | 115.4078 | 0.036186 | 0.012 | 178616.8333 | 0.15101 | 0.38342 | 1383.1667 | 0.47148 | 95.9244 | 117.7973 | 3.4682 | 0
Image_H100_BatchSize_128 | 78.4264 | 83.6663 | 25 | 15.0466 | 75.7382 | 78.2213 | 25 | 12.5157 | 75.1234 | 12.0646 | 180000.0417 | 58.6663 | 0.3991 | 0.76513 | 179971.0417 | 28.9583 | 0 | 0.041667 | 78.4363 | 0.055983 | 0.013 | 179068.4167 | 0.39241 | 0.78871 | 931.625 | 1.6854 | 58.6663 | 79.6042 | 9.0236 | 28.9583 | 5.0416 | 5.0301 | 5.1075 | 5.1075 | 5.0429 | 80.9657 | 130.6667 | 180000 | 53.2213 | 0.08733 | 0.16584 | 179999.9583 | 0 | 0 | 0.041667 | 75.7388 | 0.044723 | 0.012 | 179268.9583 | 0.086177 | 0.17095 | 731.0417 | 0.37009 | 53.2213 | 75.9027 | 8.6636 | 0
Image_H100_BatchSize_256 | 76.1735 | 79.8514 | 25 | 13.2428 | 73.6005 | 75.7339 | 25 | 11.6974 | 73.0103 | 11.4266 | 180000.0417 | 54.8514 | 0.38193 | 0.57945 | 180000 | 0 | 0 | 0.041667 | 76.1828 | 0.04776 | 0.013 | 177100.7917 | 0.37618 | 0.59064 | 2899.25 | 0.7328 | 54.8514 | 77.4792 | 2.3598 | 0 | [7 empty] | 180000 | 50.7339 | 0.083814 | 0.1264 | 179999.9583 | 0 | 0 | 0.041667 | 73.6011 | 0.040859 | 0.012 | 178318.125 | 0.083018 | 0.12811 | 1681.875 | 0.16814 | 50.7339 | 74.5362 | 3.2861 | 0
Image_H100_BatchSize_512 | 79.1215 | 86.7809 | 25 | 17.1014 | 76.3968 | 79.4821 | 25 | 13.2815 | 75.7746 | 12.7118 | 180000.0417 | 61.7809 | 0.40454 | 1.0305 | 179844.0417 | 155.9583 | 0 | 0.041667 | 79.1315 | 0.04065 | 0.013 | 177903.7917 | 0.39346 | 1.0582 | 2096.25 | 1.345 | 61.7809 | 81.1841 | 2.7203 | 155.9583 | 7.1291 | 7.1321 | 7.2095 | 7.7543 | 7.1454 | 81.3396 | 17.3802 | 180000.1667 | 54.4821 | 0.088394 | 0.22177 | 180000.125 | 0 | 0 | 0.041667 | 76.3974 | 0.041126 | 0.012 | 177786.3333 | 0.086447 | 0.22839 | 2213.8333 | 0.24474 | 54.4821 | 76.9568 | 2.5791 | 0
Image_H100_ImageSize_16 | 67.7449 | 71.116 | 25 | 11.2393 | 65.5974 | 67.406 | 25 | 9.8551 | 65.1032 | 9.599 | 180000.0417 | 46.116 | 0.3187 | 0.52051 | 180000 | 0 | 0 | 0.041667 | 67.7525 | 0.044853 | 0.013 | 178284.4167 | 0.3145 | 0.53061 | 1715.625 | 0.75487 | 46.116 | 68.082 | 3.7336 | 0 | [7 empty] | 180000 | 42.406 | 0.070171 | 0.11391 | 179999.9583 | 0 | 0 | 0.041667 | 65.5979 | 0.037836 | 0.012 | 179169.9583 | 0.069344 | 0.11572 | 830.0417 | 0.24867 | 42.406 | 65.7842 | 6.1213 | 0
Image_H100_ImageSize_32 | 78.4264 | 83.6663 | 25 | 15.0466 | 75.7382 | 78.2213 | 25 | 12.5157 | 75.1234 | 12.0646 | 180000.0417 | 58.6663 | 0.3991 | 0.76513 | 179971.0417 | 28.9583 | 0 | 0.041667 | 78.4363 | 0.055983 | 0.013 | 179068.4167 | 0.39241 | 0.78871 | 931.625 | 1.6854 | 58.6663 | 79.6042 | 9.0236 | 28.9583 | 5.0416 | 5.0301 | 5.1075 | 5.1075 | 5.0429 | 80.9657 | 130.6667 | 180000 | 53.2213 | 0.08733 | 0.16584 | 179999.9583 | 0 | 0 | 0.041667 | 75.7388 | 0.044723 | 0.012 | 179268.9583 | 0.086177 | 0.17095 | 731.0417 | 0.37009 | 53.2213 | 75.9027 | 8.6636 | 0
Image_H100_ImageSize_64 | 129.4308 | 136.1729 | 25 | 26.3779 | 124.1564 | 128.3567 | 25 | 23.815 | 122.9689 | 23.4267 | 179996.125 | 111.1729 | 0.78372 | 1.104 | 179820.1667 | 175.9167 | 0 | 0.041667 | 129.4514 | 0.062477 | 0.013 | 172848.5833 | 0.76438 | 1.1447 | 7147.5417 | 1.2514 | 111.1729 | 131.5254 | 1.3388 | 175.9167 | 7.6807 | 7.7471 | 7.8643 | 8.0009 | 7.725 | 128.8197 | 37.3016 | 179996.0833 | 103.3567 | 0.16889 | 0.23655 | 179996.0417 | 0 | 0 | 0.041667 | 124.1576 | 0.046386 | 0.012 | 173141.875 | 0.16524 | 0.24068 | 6854.2083 | 0.26101 | 103.3567 | 126.5727 | 0.96315 | 0
Image_H100_ModelSize_128 | 78.4264 | 83.6663 | 25 | 15.0466 | 75.7382 | 78.2213 | 25 | 12.5157 | 75.1234 | 12.0646 | 180000.0417 | 58.6663 | 0.3991 | 0.76513 | 179971.0417 | 28.9583 | 0 | 0.041667 | 78.4363 | 0.055983 | 0.013 | 179068.4167 | 0.39241 | 0.78871 | 931.625 | 1.6854 | 58.6663 | 79.6042 | 9.0236 | 28.9583 | 5.0416 | 5.0301 | 5.1075 | 5.1075 | 5.0429 | 80.9657 | 130.6667 | 180000 | 53.2213 | 0.08733 | 0.16584 | 179999.9583 | 0 | 0 | 0.041667 | 75.7388 | 0.044723 | 0.012 | 179268.9583 | 0.086177 | 0.17095 | 731.0417 | 0.37009 | 53.2213 | 75.9027 | 8.6636 | 0
Image_H100_ModelSize_256 | 91.2229 | 98.7009 | 25 | 19.7471 | 87.8839 | 91.1643 | 25 | 15.6473 | 87.1266 | 14.9837 | 179996.125 | 73.7009 | 0.49595 | 1.0583 | 179868.1667 | 127.9167 | 0 | 0.041667 | 91.2355 | 0.049211 | 0.013 | 178464 | 0.4867 | 1.0955 | 1532.125 | 1.574 | 73.7009 | 94.9284 | 4.657 | 127.9167 | 7.6368 | 7.6573 | 7.7502 | 7.8111 | 7.6453 | 92.6209 | 39.7508 | 180000 | 66.1643 | 0.10764 | 0.22701 | 179999.9583 | 0 | 0 | 0.041667 | 87.8847 | 0.041143 | 0.012 | 179614.9583 | 0.10654 | 0.23153 | 385.0417 | 0.62392 | 66.1643 | 87.9493 | 14.5919 | 0
Image_H100_ModelSize_512 | 93.4798 | 103.0349 | 25 | 21.8901 | 90.0238 | 94.1715 | 25 | 16.6126 | 89.2431 | 15.9417 | 180000.0417 | 78.0349 | 0.51342 | 1.2422 | 179956 | 3.125 | 40.875 | 0.041667 | 93.4931 | 0.042846 | 0.013 | 177944.4167 | 0.5023 | 1.2556 | 2055.625 | 1.4753 | 78.0349 | 98.7006 | 3.0521 | 44 | 10.2679 | 10.3348 | 10.5474 | 10.5474 | 10.3087 | 95.495 | 89.6368 | 180000 | 69.1715 | 0.111 | 0.26511 | 179999.9583 | 0 | 0 | 0.041667 | 90.0246 | 0.042333 | 0.012 | 179358.4583 | 0.10985 | 0.27318 | 641.5417 | 0.43141 | 69.1715 | 92.0379 | 9.1672 | 0
Text_B200_BatchSize16 | 204.8693 | 217.7443 | 25 | 44.3459 | 195.7516 | 204.7673 | 25 | 42.196 | 193.7331 | 41.9812 | 180000.0417 | 192.7443 | 1.356 | 1.7889 | 179600.0417 | 4 | 395.9583 | 0.041667 | 204.9076 | 0.03783 | 0.013 | 177186.0417 | 1.3253 | 1.8782 | 2814 | 3.2861 | 192.7443 | 206.7932 | 1.7809 | 399.9583 | 11.8098 | 11.7871 | 12.2201 | 17.7853 | 13.186 | 203.2275 | 5.8517 | 180000 | 179.7673 | 0.28742 | 0.37669 | 179996.0833 | 3.875 | 0 | 0.041667 | 195.7538 | 0.03514 | 0.012 | 177174.75 | 0.28186 | 0.39369 | 2825.25 | 0.63643 | 179.7673 | 196.4253 | 1.5863 | 3.875 | 7.1094 | 7.2133 | 7.2133 | 7.2133 | 7.1699 | 198.7397 | 62.7268
Text_B200_BatchSize2 | 119.7982 | 124.522 | 25 | 22.1717 | 115.0197 | 118.9433 | 25 | 21.266 | 113.9349 | 21.2422 | 180000.0417 | 99.522 | 0.7097 | 0.77553 | 179996.4583 | 3.5417 | 0 | 0.041667 | 119.8163 | 0.042189 | 0.013 | 177415.25 | 0.70589 | 0.8093 | 2584.7917 | 0.97088 | 99.522 | 120.1389 | 2.1935 | 3.5417 | 5.1597 | 5.1655 | 5.1655 | 5.1655 | 5.1602 | 121.7805 | 53.993 | 180000 | 93.9433 | 0.15418 | 0.16823 | 179999.9583 | 0 | 0 | 0.041667 | 115.0208 | 0.037052 | 0.028 | 177430.7083 | 0.15346 | 0.17534 | 2569.2917 | 0.20394 | 93.9433 | 116.0953 | 1.8229 | 0
Text_B200_BatchSize32 | 224.5887 | 235.6393 | 25 | 47.9558 | 214.4588 | 221.912 | 25 | 45.102 | 212.2235 | 44.4882 | 180000.0417 | 210.6393 | 1.5067 | 1.8776 | 179579.8333 | 20.2083 | 399.9583 | 0.041667 | 224.6318 | 0.053552 | 0.013 | 177520.8333 | 1.4703 | 1.9571 | 2479.2083 | 4.1134 | 210.6393 | 225.6918 | 3.1601 | 420.1667 | 12.2286 | 12.5095 | 13.0505 | 13.2579 | 12.5307 | 222.3051 | 12.0919 | 180000 | 196.912 | 0.3184 | 0.3947 | 179999.9583 | 0 | 0 | 0.041667 | 214.4613 | 0.058376 | 0.012 | 177392.625 | 0.31191 | 0.41125 | 2607.375 | 0.75998 | 196.912 | 215.2656 | 3.3289 | 0
Text_B200_Deepspeedds_z1 | 196.2231 | 210.994 | 25 | 43.2779 | 187.5467 | 197.4787 | 25 | 40.5817 | 185.6245 | 40.33 | 180000.0417 | 185.994 | 1.2903 | 1.8752 | 179583.9167 | 4.1667 | 408.375 | 3.5833 | 196.2594 | 0.037401 | 0.013 | 177912.0833 | 1.2481 | 1.9656 | 2087.9583 | 4.8861 | 185.994 | 198.1097 | 2.4213 | 416.0833 | 12.8913 | 12.8821 | 13.1489 | 20.5172 | 15.0557 | 195.4383 | 5.3496 | 180000 | 172.4787 | 0.27368 | 0.39574 | 179996.0833 | 3.875 | 0 | 0.041667 | 187.5488 | 0.035184 | 0.012 | 177932.375 | 0.26611 | 0.41345 | 2067.625 | 0.92553 | 172.4787 | 187.6966 | 2.2288 | 3.875 | 9.2376 | 9.3825 | 9.3825 | 9.3825 | 9.3249 | 190.4319 | 90.3303
Text_B200_Deepspeedds_z2 | 201.906 | 214.2379 | 25 | 43.6589 | 192.9388 | 201.4499 | 25 | 41.264 | 190.9526 | 40.7911 | 180000.0417 | 189.2379 | 1.3335 | 1.7761 | 179592.0417 | 12 | 395.9583 | 0.041667 | 201.9436 | 0.041055 | 0.013 | 177238.4583 | 1.3026 | 1.8819 | 2761.5833 | 3.3156 | 189.2379 | 203.7017 | 2.0173 | 407.9583 | 11.7107 | 11.7452 | 12.1925 | 16.5328 | 12.5003 | 200.2579 | 7.1847 | 180000 | 176.4499 | 0.28282 | 0.3742 | 179996.1667 | 3.7917 | 0 | 0.041667 | 192.9409 | 0.035993 | 0.012 | 177301.0833 | 0.27724 | 0.39528 | 2698.9167 | 0.64924 | 176.4499 | 193.4359 | 1.7082 | 3.7917 | 6.2284 | 6.278 | 6.278 | 6.278 | 6.2489 | 196.9944 | 54.741
Text_B200_Deepspeedds_z3 | 204.8693 | 217.7443 | 25 | 44.3459 | 195.7516 | 204.7673 | 25 | 42.196 | 193.7331 | 41.9812 | 180000.0417 | 192.7443 | 1.356 | 1.7889 | 179600.0417 | 4 | 395.9583 | 0.041667 | 204.9076 | 0.03783 | 0.013 | 177186.0417 | 1.3253 | 1.8782 | 2814 | 3.2861 | 192.7443 | 206.7932 | 1.7809 | 399.9583 | 11.8098 | 11.7871 | 12.2201 | 17.7853 | 13.186 | 203.2275 | 5.8517 | 180000 | 179.7673 | 0.28742 | 0.37669 | 179996.0833 | 3.875 | 0 | 0.041667 | 195.7538 | 0.03514 | 0.012 | 177174.75 | 0.28186 | 0.39369 | 2825.25 | 0.63643 | 179.7673 | 196.4253 | 1.5863 | 3.875 | 7.1094 | 7.2133 | 7.2133 | 7.2133 | 7.1699 | 198.7397 | 62.7268
Text_B200_Lamma_1B | 126.0131 | 133.7276 | 25 | 26.1566 | 120.9148 | 125.1374 | 25 | 23.0587 | 119.7634 | 22.5235 | 180000.0417 | 108.7276 | 0.75741 | 1.1928 | 179208.0417 | 791.9583 | 0 | 0.041667 | 126.0329 | 0.045546 | 0.013 | 178972.1667 | 0.72836 | 1.2377 | 1027.875 | 5.8152 | 108.7276 | 126.89 | 6.3131 | 791.9583 | 7.1607 | 7.187 | 7.3985 | 7.8583 | 7.1943 | 126.3849 | 5.8911 | 180000 | 100.1374 | 0.1637 | 0.25561 | 179999.9583 | 0 | 0 | 0.041667 | 120.9159 | 0.037471 | 0.012 | 178979.375 | 0.15848 | 0.26511 | 1020.625 | 1.0797 | 100.1374 | 121.3065 | 4.8959 | 0
Text_B200_Lamma_3B | 156.3431 | 166.2868 | 25 | 33.2793 | 149.6995 | 155.5338 | 25 | 29.9444 | 148.2133 | 29.3624 | 180000.0417 | 141.2868 | 0.98747 | 1.4874 | 179480.0833 | 508.6667 | 11.25 | 0.041667 | 156.3699 | 0.0381 | 0.013 | 178240.1667 | 0.95861 | 1.5809 | 1759.875 | 3.9111 | 141.2868 | 158.6439 | 2.9143 | 519.9167 | 9.5909 | 9.6022 | 9.9832 | 11.7182 | 9.7081 | 156.1889 | 5.822 | 180000 | 130.5338 | 0.21146 | 0.31579 | 179999.9583 | 0 | 0 | 0.041667 | 149.7011 | 0.034983 | 0.012 | 178237.375 | 0.20625 | 0.33381 | 1762.625 | 0.73841 | 130.5338 | 150.2968 | 2.5605 | 0
Text_B200_Lamma_8B | 204.8693 | 217.7443 | 25 | 44.3459 | 195.7516 | 204.7673 | 25 | 42.196 | 193.7331 | 41.9812 | 180000.0417 | 192.7443 | 1.356 | 1.7889 | 179600.0417 | 4 | 395.9583 | 0.041667 | 204.9076 | 0.03783 | 0.013 | 177186.0417 | 1.3253 | 1.8782 | 2814 | 3.2861 | 192.7443 | 206.7932 | 1.7809 | 399.9583 | 11.8098 | 11.7871 | 12.2201 | 17.7853 | 13.186 | 203.2275 | 5.8517 | 180000 | 179.7673 | 0.28742 | 0.37669 | 179996.0833 | 3.875 | 0 | 0.041667 | 195.7538 | 0.03514 | 0.012 | 177174.75 | 0.28186 | 0.39369 | 2825.25 | 0.63643 | 179.7673 | 196.4253 | 1.5863 | 3.875 | 7.1094 | 7.2133 | 7.2133 | 7.2133 | 7.1699 | 198.7397 | 62.7268
Text_B200_SeqLength_1024 | 204.7448 | 216.7736 | 25 | 44.155 | 195.6319 | 203.8488 | 25 | 41.7026 | 193.6144 | 41.3753 | 180000.0417 | 191.7736 | 1.3552 | 1.7884 | 179596.0417 | 8 | 395.9583 | 0.041667 | 204.7831 | 0.038737 | 0.013 | 177179.625 | 1.3243 | 1.8837 | 2820.4167 | 3.2967 | 191.7736 | 206.5746 | 1.837 | 403.9583 | 11.8126 | 11.8897 | 12.3268 | 15.9106 | 12.3377 | 203.1265 | 6.207 | 180000 | 178.8488 | 0.28729 | 0.37666 | 179996.3333 | 3.625 | 0 | 0.041667 | 195.6341 | 0.036997 | 0.012 | 177106.1667 | 0.28167 | 0.39599 | 2893.8333 | 0.63116 | 178.8488 | 196.3782 | 1.6674 | 3.625 | 5.4083 | 5.4244 | 5.4244 | 5.4244 | 5.411 | 200.7261 | 73.8226
Text_B200_SeqLength_2048 | 204.8693 | 217.7443 | 25 | 44.3459 | 195.7516 | 204.7673 | 25 | 42.196 | 193.7331 | 41.9812 | 180000.0417 | 192.7443 | 1.356 | 1.7889 | 179600.0417 | 4 | 395.9583 | 0.041667 | 204.9076 | 0.03783 | 0.013 | 177186.0417 | 1.3253 | 1.8782 | 2814 | 3.2861 | 192.7443 | 206.7932 | 1.7809 | 399.9583 | 11.8098 | 11.7871 | 12.2201 | 17.7853 | 13.186 | 203.2275 | 5.8517 | 180000 | 179.7673 | 0.28742 | 0.37669 | 179996.0833 | 3.875 | 0 | 0.041667 | 195.7538 | 0.03514 | 0.012 | 177174.75 | 0.28186 | 0.39369 | 2825.25 | 0.63643 | 179.7673 | 196.4253 | 1.5863 | 3.875 | 7.1094 | 7.2133 | 7.2133 | 7.2133 | 7.1699 | 198.7397 | 62.7268
Text_B200_SeqLength_4096 | 204.9353 | 217.3004 | 25 | 44.1867 | 195.813 | 204.2626 | 25 | 41.8141 | 193.7935 | 41.5276 | 180000.0417 | 192.3004 | 1.3566 | 1.7904 | 179596.125 | 7.9167 | 395.9583 | 0.041667 | 204.9737 | 0.039568 | 0.013 | 177209.9583 | 1.3259 | 1.8633 | 2790.0833 | 3.3096 | 192.3004 | 206.7996 | 1.9113 | 403.875 | 11.807 | 11.8603 | 12.2971 | 16.4076 | 12.5071 | 203.2508 | 6.6439 | 180000 | 179.2626 | 0.28757 | 0.37702 | 179996.25 | 3.7083 | 0 | 0.041667 | 195.8152 | 0.035485 | 0.012 | 177165.25 | 0.28198 | 0.39171 | 2834.75 | 0.6368 | 179.2626 | 196.5537 | 1.6046 | 3.7083 | 5.8726 | 5.8978 | 5.8978 | 5.8978 | 5.8792 | 200.5724 | 47.8563
Text_H100_BatchSize16 | 163.1904 | 170.6615 | 25 | 32.9138 | 156.2022 | 161.3373 | 25 | 31.1426 | 154.6365 | 30.8462 | 180000.0417 | 145.6615 | 1.0386 | 1.265 | 179732 | 268 | 0 | 0.041667 | 163.2183 | 0.055709 | 0.013 | 177092.2083 | 1.0175 | 1.3318 | 2907.8333 | 2.3244 | 145.6615 | 164.0385 | 2.8338 | 268 | 8.8485 | 8.8654 | 9.1792 | 9.3235 | 8.8756 | 161.273 | 18.7615 | 180000 | 136.3373 | 0.22274 | 0.27032 | 179999.9583 | 0 | 0 | 0.041667 | 156.2038 | 0.052299 | 0.012 | 177105.6667 | 0.21892 | 0.28408 | 2894.3333 | 0.45679 | 136.3373 | 156.3347 | 2.6203 | 0
Text_H100_BatchSize2 | 91.3422 | 94.9626 | 25 | 15.4104 | 88.0051 | 90.9217 | 25 | 15.0095 | 87.2414 | 14.9705 | 180000.0417 | 69.9626 | 0.49541 | 0.55377 | 180000 | 0 | 0 | 0.041667 | 91.3544 | 0.044146 | 0.013 | 176937.2917 | 0.492 | 0.59402 | 3062.75 | 0.69249 | 69.9626 | 91.5153 | 1.9837 | 0 | [7 empty] | 180000 | 65.9217 | 0.10847 | 0.1211 | 179999.9583 | 0 | 0 | 0.041667 | 88.0058 | 0.037922 | 0.012 | 176910.5 | 0.10782 | 0.13009 | 3089.5 | 0.1459 | 65.9217 | 88.3515 | 1.5878 | 0
Text_H100_BatchSize32 | 169.9807 | 177.5836 | 25 | 34.4764 | 162.6464 | 167.9622 | 25 | 32.7285 | 161.0057 | 32.4237 | 180000.0417 | 152.5836 | 1.0901 | 1.3084 | 179748.0833 | 251.9167 | 0 | 0.041667 | 170.0102 | 0.057843 | 0.013 | 177446.75 | 1.0691 | 1.3656 | 2553.2917 | 2.551 | 152.5836 | 170.8009 | 3.3526 | 251.9167 | 9.2376 | 9.2419 | 9.5055 | 9.6029 | 9.2557 | 167.9175 | 20.2376 | 180000 | 142.9622 | 0.23346 | 0.27933 | 179999.9583 | 0 | 0 | 0.041667 | 162.6482 | 0.055779 | 0.012 | 177446.7917 | 0.22966 | 0.29124 | 2553.2083 | 0.49733 | 142.9622 | 163.0479 | 3.2109 | 0
Text_H100_Deepspeedds_z1 | 153.7551 | 162.2481 | 25 | 32.1059 | 147.2449 | 152.4817 | 25 | 29.1761 | 145.7858 | 28.7108 | 180000.0417 | 137.2481 | 0.96756 | 1.38 | 179415.5833 | 580.9583 | 3.4583 | 0.041667 | 153.7811 | 0.045559 | 0.013 | 178619.75 | 0.93199 | 1.3981 | 1380.2917 | 5.5709 | 137.2481 | 154.4545 | 4.678 | 584.4167 | 7.554 | 6.3309 | 9.89 | 10.4713 | 9.3537 | 153.4188 | 6.5904 | 180000 | 127.4817 | 0.20758 | 0.29388 | 179999.9583 | 0 | 0 | 0.041667 | 147.2464 | 0.045173 | 0.012 | 178619.2917 | 0.20118 | 0.29783 | 1380.7083 | 1.0356 | 127.4817 | 147.3304 | 4.6115 | 0
Text_H100_Deepspeedds_z2 | 159.2257 | 166.7905 | 25 | 32.0421 | 152.4395 | 157.5257 | 25 | 30.2712 | 150.9178 | 29.9388 | 180000.0417 | 141.7905 | 1.0086 | 1.2457 | 179720.0417 | 279.9583 | 0 | 0.041667 | 159.2528 | 0.053576 | 0.013 | 176884.7917 | 0.9861 | 1.3497 | 3115.25 | 2.284 | 141.7905 | 160.1633 | 2.5224 | 279.9583 | 8.6847 | 8.7287 | 9.0553 | 9.4164 | 8.7518 | 157.4746 | 16.6207 | 180000 | 132.5257 | 0.21648 | 0.26643 | 179999.9583 | 0 | 0 | 0.041667 | 152.441 | 0.043633 | 0.012 | 176883.4167 | 0.21239 | 0.28272 | 3116.5833 | 0.44817 | 132.5257 | 152.6231 | 1.935 | 0
Text_H100_Deepspeedds_z3 | 163.1904 | 170.6615 | 25 | 32.9138 | 156.2022 | 161.3373 | 25 | 31.1426 | 154.6365 | 30.8462 | 180000.0417 | 145.6615 | 1.0386 | 1.265 | 179732 | 268 | 0 | 0.041667 | 163.2183 | 0.055709 | 0.013 | 177092.2083 | 1.0175 | 1.3318 | 2907.8333 | 2.3244 | 145.6615 | 164.0385 | 2.8338 | 268 | 8.8485 | 8.8654 | 9.1792 | 9.3235 | 8.8756 | 161.273 | 18.7615 | 180000 | 136.3373 | 0.22274 | 0.27032 | 179999.9583 | 0 | 0 | 0.041667 | 156.2038 | 0.052299 | 0.012 | 177105.6667 | 0.21892 | 0.28408 | 2894.3333 | 0.45679 | 136.3373 | 156.3347 | 2.6203 | 0
Text_H100_Lamma_1B | 109.1621 | 116.1092 | 25 | 22.2529 | 104.9181 | 108.6725 | 25 | 19.2397 | 103.9562 | 18.7836 | 180000.0417 | 91.1092 | 0.63038 | 1.0422 | 179288.0833 | 711.9167 | 0 | 0.041667 | 109.1783 | 0.038967 | 0.013 | 178779.8333 | 0.60382 | 1.0983 | 1220.2083 | 4.5207 | 91.1092 | 110.5192 | 4.3402 | 711.9167 | 6.9813 | 6.9811 | 7.187 | 7.7804 | 7.0042 | 109.4008 | 4.8081 | 180000 | 83.6725 | 0.13672 | 0.22432 | 179999.9583 | 0 | 0 | 0.041667 | 104.9191 | 0.038287 | 0.012 | 178743.0417 | 0.13188 | 0.23418 | 1256.9583 | 0.82483 | 83.6725 | 105.4084 | 4.0858 | 0
Text_H100_Lamma_3B | 138.6865 | 146.3645 | 25 | 28.1975 | 132.944 | 137.7472 | 25 | 25.9166 | 131.6521 | 25.5371 | 180000.0417 | 121.3645 | 0.85328 | 1.187 | 179572 | 428 | 0 | 0.041667 | 138.7091 | 0.038949 | 0.013 | 177413.8333 | 0.83105 | 1.2466 | 2586.2083 | 2.3788 | 121.3645 | 140.1737 | 2.0186 | 428 | 8.1952 | 8.1842 | 8.4472 | 9.612 | 8.2482 | 137.7954 | 6.3665 | 180000 | 112.7472 | 0.18374 | 0.25419 | 179999.9583 | 0 | 0 | 0.041667 | 132.9453 | 0.036887 | 0.012 | 177353.0417 | 0.17965 | 0.26808 | 2646.9583 | 0.4575 | 112.7472 | 133.4782 | 1.8141 | 0
Text_H100_Lamma_8B | 163.1904 | 170.6615 | 25 | 32.9138 | 156.2022 | 161.3373 | 25 | 31.1426 | 154.6365 | 30.8462 | 180000.0417 | 145.6615 | 1.0386 | 1.265 | 179732 | 268 | 0 | 0.041667 | 163.2183 | 0.055709 | 0.013 | 177092.2083 | 1.0175 | 1.3318 | 2907.8333 | 2.3244 | 145.6615 | 164.0385 | 2.8338 | 268 | 8.8485 | 8.8654 | 9.1792 | 9.3235 | 8.8756 | 161.273 | 18.7615 | 180000 | 136.3373 | 0.22274 | 0.27032 | 179999.9583 | 0 | 0 | 0.041667 | 156.2038 | 0.052299 | 0.012 | 177105.6667 | 0.21892 | 0.28408 | 2894.3333 | 0.45679 | 136.3373 | 156.3347 | 2.6203 | 0
Text_H100_SeqLength_1024 | 163.1132 | 170.5563 | 25 | 32.8974 | 156.129 | 161.3265 | 25 | 31.2284 | 154.5642 | 30.8987 | 180000.0417 | 145.5563 | 1.038 | 1.2642 | 179728 | 272 | 0 | 0.041667 | 163.1412 | 0.06258 | 0.013 | 177116 | 1.0166 | 1.3363 | 2884.0417 | 2.3515 | 145.5563 | 163.9016 | 3.2852 | 272 | 8.8233 | 8.8293 | 9.1756 | 9.3246 | 8.8573 | 161.1993 | 23.0097 | 180000 | 136.3265 | 0.22262 | 0.27016 | 179999.9583 | 0 | 0 | 0.041667 | 156.1306 | 0.050454 | 0.012 | 177075.0417 | 0.21874 | 0.28511 | 2924.9583 | 0.45784 | 136.3265 | 156.3735 | 2.4812 | 0
Text_H100_SeqLength_2048 | 163.1904 | 170.6615 | 25 | 32.9138 | 156.2022 | 161.3373 | 25 | 31.1426 | 154.6365 | 30.8462 | 180000.0417 | 145.6615 | 1.0386 | 1.265 | 179732 | 268 | 0 | 0.041667 | 163.2183 | 0.055709 | 0.013 | 177092.2083 | 1.0175 | 1.3318 | 2907.8333 | 2.3244 | 145.6615 | 164.0385 | 2.8338 | 268 | 8.8485 | 8.8654 | 9.1792 | 9.3235 | 8.8756 | 161.273 | 18.7615 | 180000 | 136.3373 | 0.22274 | 0.27032 | 179999.9583 | 0 | 0 | 0.041667 | 156.2038 | 0.052299 | 0.012 | 177105.6667 | 0.21892 | 0.28408 | 2894.3333 | 0.45679 | 136.3373 | 156.3347 | 2.6203 | 0
Text_H100_SeqLength_4096 | 162.7822 | 170.2583 | 25 | 32.8181 | 155.8148 | 160.9118 | 25 | 31.0669 | 154.2537 | 30.7764 | 180000.0417 | 145.2583 | 1.0355 | 1.2644 | 179732 | 268 | 0 | 0.041667 | 162.8101 | 0.058005 | 0.013 | 177109.875 | 1.0142 | 1.3331 | 2890.1667 | 2.3448 | 145.2583 | 163.6373 | 2.9947 | 268 | 8.8474 | 8.8653 | 9.179 | 9.338 | 8.8738 | 160.8854 | 20.2737 | 180000 | 135.9118 | 0.22209 | 0.27022 | 179999.9583 | 0 | 0 | 0.041667 | 155.8164 | 0.054759 | 0.012 | 177084.4167 | 0.21821 | 0.28444 | 2915.5833 | 0.45769 | 135.9118 | 156.0609 | 2.756 | 0

## Nf_results
scenario | Mission_duration_s | IGBT_Nf_eq | IGBT_Nf_eq_dT_ge10 | IGBT_Nf_eq_dT_lt10 | IGBT_Nf_eq_load_cycles | IGBT_Nf_eq_grid_cycles | IGBT_Nf_worst_cycle | IGBT_worst_cycle_dT_K | IGBT_worst_cycle_Tmean_C | Diode_Nf_eq | Diode_Nf_eq_dT_ge10 | Diode_Nf_eq_dT_lt10 | Diode_Nf_eq_load_cycles | Diode_Nf_eq_grid_cycles | Diode_Nf_worst_cycle | Diode_worst_cycle_dT_K | Diode_worst_cycle_Tmean_C | Limiting_device | IGBT_lifetime_years_actual | Diode_lifetime_years_actual
Image_B200_BatchSize_128 | 43200 | 231803.9363 | inf | 231803.9363 | 231803.9363 | 3.9218e+25 | 115901.976 | 86.6634 | 68.3317 | 195438.5246 | inf | 195438.5246 | 195438.5246 | 1.2218e+36 | 97719.2623 | 78.7059 | 64.353 | Diode | 317.5396 | 267.724
Image_B200_BatchSize_256 | 43200 | 212438.2005 | inf | 212438.2005 | 212438.2005 | 4.5262e+24 | 106219.2837 | 88.0589 | 69.0294 | 193309.7651 | inf | 193309.7651 | 193309.7651 | 1.8915e+35 | 96654.8825 | 78.8657 | 64.4329 | Diode | 291.0112 | 264.8079
Image_B200_BatchSize_512 | 43200 | 193081.0952 | inf | 193081.0952 | 193081.0952 | 1.1602e+24 | 96541.772 | 89.6089 | 69.8045 | 184396.8605 | inf | 184396.8605 | 184396.8605 | 5.8416e+34 | 92198.4302 | 79.5578 | 64.7789 | Diode | 264.4947 | 252.5984
Image_B200_ImageSize_128 | 43200 | 3854.4936 | inf | 3854.4936 | 3854.4936 | 6.3821e+22 | 1927.2474 | 175.1238 | 112.5619 | 2791.4429 | inf | 2791.4429 | 2791.4429 | 2.7657e+33 | 1395.7215 | 164.9394 | 107.4697 | Diode | 5.2801 | 3.8239
Image_B200_ImageSize_32 | 43200 | 231803.9363 | inf | 231803.9363 | 231803.9363 | 3.9218e+25 | 115901.976 | 86.6634 | 68.3317 | 195438.5246 | inf | 195438.5246 | 195438.5246 | 1.2218e+36 | 97719.2623 | 78.7059 | 64.353 | Diode | 317.5396 | 267.724
Image_B200_ImageSize_64 | 43200 | 16514.4068 | inf | 16514.4068 | 16514.4068 | 5.6821e+22 | 8257.2487 | 137.8751 | 93.9375 | 13277.7293 | inf | 13277.7293 | 13277.7293 | 3.0004e+33 | 6638.8647 | 127.2169 | 88.6084 | Diode | 22.6225 | 18.1887
Image_B200_ModelSize_128 | 43200 | 231803.9363 | inf | 231803.9363 | 231803.9363 | 3.9218e+25 | 115901.976 | 86.6634 | 68.3317 | 195438.5246 | inf | 195438.5246 | 195438.5246 | 1.2218e+36 | 97719.2623 | 78.7059 | 64.353 | Diode | 317.5396 | 267.724
Image_B200_ModelSize_256 | 43200 | 98461.7185 | inf | 98461.7185 | 98461.7185 | 2.4623e+23 | 49231.5929 | 101.1956 | 75.5978 | 90780.1294 | inf | 90780.1294 | 90780.1294 | 1.3759e+34 | 45390.0647 | 90.6196 | 70.3098 | Diode | 134.8791 | 124.3563
Image_B200_ModelSize_512 | 43200 | 66589.227 | inf | 66589.227 | 66589.227 | 1.3652e+22 | 33307.5102 | 108.46 | 79.23 | 66324.2577 | inf | 66324.2577 | 66324.2577 | 8.9872e+32 | 33162.1289 | 95.9244 | 72.9622 | Diode | 91.2181 | 90.8551
Image_H100_BatchSize_128 | 43200 | 1925453.7447 | inf | 1925453.7447 | 1925453.7447 | 4.2275e+28 | 962726.8729 | 58.6663 | 54.3332 | 1668505.8208 | inf | 1668505.8208 | 1668505.8208 | 6.7466e+38 | 834252.9104 | 53.2213 | 51.6106 | Diode | 2637.6079 | 2285.6244
Image_H100_BatchSize_256 | 43200 | 2808296.3504 | inf | 2808296.3504 | 2808296.3504 | 2.5084e+30 | 1404148.1752 | 54.8514 | 52.4257 | 2204463.8062 | inf | 2204463.8062 | 2204463.8062 | 2.5847e+40 | 1102231.9031 | 50.7339 | 50.3669 | Diode | 3846.9813 | 3019.8134
Image_H100_BatchSize_512 | 43200 | 1447711.0638 | inf | 1447711.0638 | 1447711.0638 | 6.6208e+26 | 723855.7163 | 61.7809 | 55.8904 | 1459168.9029 | inf | 1459168.9029 | 1459168.9029 | 1.6449e+37 | 729584.4514 | 54.4821 | 52.241 | IGBT | 1983.1658 | 1998.8615
Image_H100_ImageSize_16 | 43200 | 7852905.2212 | inf | 7852905.2212 | 7852905.2212 | 2.9536e+31 | 3926452.6106 | 46.116 | 48.058 | 6719049.5426 | inf | 6719049.5426 | 6719049.5426 | 2.7861e+41 | 3359524.7713 | 42.406 | 46.203 | Diode | 10757.4044 | 9204.1775
Image_H100_ImageSize_32 | 43200 | 1925453.7447 | inf | 1925453.7447 | 1925453.7447 | 4.2275e+28 | 962726.8729 | 58.6663 | 54.3332 | 1668505.8208 | inf | 1668505.8208 | 1668505.8208 | 6.7466e+38 | 834252.9104 | 53.2213 | 51.6106 | Diode | 2637.6079 | 2285.6244
Image_H100_ImageSize_64 | 43200 | 57881.1874 | inf | 57881.1874 | 57881.1874 | 1.6389e+25 | 28940.5976 | 111.1729 | 80.5865 | 43727.9094 | inf | 43727.9094 | 43727.9094 | 4.463e+35 | 21863.9547 | 103.3567 | 76.6783 | Diode | 79.2893 | 59.9012
Image_H100_ModelSize_128 | 43200 | 1925453.7447 | inf | 1925453.7447 | 1925453.7447 | 4.2275e+28 | 962726.8729 | 58.6663 | 54.3332 | 1668505.8208 | inf | 1668505.8208 | 1668505.8208 | 6.7466e+38 | 834252.9104 | 53.2213 | 51.6106 | Diode | 2637.6079 | 2285.6244
Image_H100_ModelSize_256 | 43200 | 557024.6093 | inf | 557024.6093 | 557024.6093 | 1.0569e+26 | 278512.4071 | 73.7009 | 61.8505 | 498401.2527 | inf | 498401.2527 | 498401.2527 | 2.922e+36 | 249200.6264 | 66.1643 | 58.0822 | Diode | 763.0474 | 682.7414
Image_H100_ModelSize_512 | 43200 | 409363.9679 | inf | 409363.9679 | 409363.9679 | 8.7202e+24 | 204685.2125 | 78.0349 | 64.0175 | 391978.6521 | inf | 391978.6521 | 391978.6521 | 2.6034e+35 | 195989.326 | 69.1715 | 59.5857 | Diode | 560.7726 | 536.9571
Text_B200_BatchSize16 | 43200 | 2113.284 | inf | 2113.284 | 2113.284 | 1.6781e+21 | 1056.8394 | 192.7443 | 121.3721 | 1637.3171 | inf | 1637.3171 | 1637.3171 | 1.2047e+32 | 818.6585 | 179.7673 | 114.8836 | Diode | 2.8949 | 2.2429
Text_B200_BatchSize2 | 43200 | 108083.1665 | inf | 108083.1665 | 108083.1665 | 5.4878e+27 | 54041.5833 | 99.522 | 74.761 | 74444.2168 | inf | 74444.2168 | 74444.2168 | 8.2125e+37 | 37222.1084 | 93.9433 | 71.9717 | Diode | 148.0591 | 101.9784
Text_B200_BatchSize32 | 43200 | 1201.2783 | inf | 1201.2783 | 1201.2783 | 5.3834e+20 | 600.6846 | 210.6393 | 130.3196 | 923.0246 | inf | 923.0246 | 923.0246 | 4.2823e+31 | 461.5123 | 196.912 | 123.456 | Diode | 1.6456 | 1.2644
Text_B200_Deepspeedds_z1 | 43200 | 2642.9045 | inf | 2642.9045 | 2642.9045 | 1.4621e+21 | 1322.9082 | 185.994 | 117.997 | 2118.1977 | inf | 2118.1977 | 2118.1977 | 1.134e+32 | 1059.0989 | 172.4787 | 111.2393 | Diode | 3.6204 | 2.9016
Text_B200_Deepspeedds_z2 | 43200 | 2372.9555 | inf | 2372.9555 | 2372.9555 | 2.0008e+21 | 1186.6001 | 189.2379 | 119.6189 | 1838.9034 | inf | 1838.9034 | 1838.9034 | 1.4165e+32 | 919.4517 | 176.4499 | 113.2249 | Diode | 3.2506 | 2.519
Text_B200_Deepspeedds_z3 | 43200 | 2113.284 | inf | 2113.284 | 2113.284 | 1.6781e+21 | 1056.8394 | 192.7443 | 121.3721 | 1637.3171 | inf | 1637.3171 | 1637.3171 | 1.2047e+32 | 818.6585 | 179.7673 | 114.8836 | Diode | 2.8949 | 2.2429
Text_B200_Lamma_1B | 43200 | 65689.7891 | inf | 65689.7891 | 65689.7891 | 1.0241e+25 | 32844.8998 | 108.7276 | 79.3638 | 52212.7906 | inf | 52212.7906 | 52212.7906 | 3.3034e+35 | 26106.3953 | 100.1374 | 75.0687 | Diode | 89.986 | 71.5244
Text_B200_Lamma_3B | 43200 | 14274.0974 | inf | 14274.0974 | 14274.0974 | 1.0097e+23 | 7137.0997 | 141.2868 | 95.6434 | 11415.1231 | inf | 11415.1231 | 11415.1231 | 5.004e+33 | 5707.5615 | 130.5338 | 90.2669 | Diode | 19.5536 | 15.6372
Text_B200_Lamma_8B | 43200 | 2113.284 | inf | 2113.284 | 2113.284 | 1.6781e+21 | 1056.8394 | 192.7443 | 121.3721 | 1637.3171 | inf | 1637.3171 | 1637.3171 | 1.2047e+32 | 818.6585 | 179.7673 | 114.8836 | Diode | 2.8949 | 2.2429
Text_B200_SeqLength_1024 | 43200 | 2181.9784 | inf | 2181.9784 | 2181.9784 | 1.7076e+21 | 1091.0772 | 191.7736 | 120.8868 | 1690.5041 | inf | 1690.5041 | 1690.5041 | 1.2272e+32 | 845.2521 | 178.8488 | 114.4244 | Diode | 2.989 | 2.3158
Text_B200_SeqLength_2048 | 43200 | 2113.284 | inf | 2113.284 | 2113.284 | 1.6781e+21 | 1056.8394 | 192.7443 | 121.3721 | 1637.3171 | inf | 1637.3171 | 1637.3171 | 1.2047e+32 | 818.6585 | 179.7673 | 114.8836 | Diode | 2.8949 | 2.2429
Text_B200_SeqLength_4096 | 43200 | 2144.4752 | inf | 2144.4752 | 2144.4752 | 1.6769e+21 | 1072.3416 | 192.3004 | 121.1502 | 1666.3055 | inf | 1666.3055 | 1666.3055 | 1.2063e+32 | 833.1528 | 179.2626 | 114.6313 | Diode | 2.9376 | 2.2826
Text_H100_BatchSize16 | 43200 | 11889.3523 | inf | 11889.3523 | 11889.3523 | 1.1861e+24 | 5944.6809 | 145.6615 | 97.8307 | 8826.4647 | inf | 8826.4647 | 8826.4647 | 4.007e+34 | 4413.2324 | 136.3373 | 93.1687 | Diode | 16.2868 | 12.091
Text_H100_BatchSize2 | 43200 | 737324.4645 | inf | 737324.4645 | 737324.4645 | 3.0596e+30 | 368662.2322 | 69.9626 | 59.9813 | 508418.9958 | inf | 508418.9958 | 508418.9958 | 2.9131e+40 | 254209.4979 | 65.9217 | 57.9608 | Diode | 1010.0335 | 696.4644
Text_H100_BatchSize32 | 43200 | 8982.5808 | inf | 8982.5808 | 8982.5808 | 5.7142e+23 | 4491.2961 | 152.5836 | 101.2918 | 6650.9599 | inf | 6650.9599 | 6650.9599 | 2.103e+34 | 3325.48 | 142.9622 | 96.4811 | Diode | 12.3049 | 9.1109
Text_H100_Deepspeedds_z1 | 43200 | 16968.2086 | inf | 16968.2086 | 16968.2086 | 4.459e+23 | 8484.1495 | 137.2481 | 93.624 | 13116.9403 | inf | 13116.9403 | 13116.9403 | 1.8869e+34 | 6558.4702 | 127.4817 | 88.7409 | Diode | 23.2441 | 17.9684
Text_H100_Deepspeedds_z2 | 43200 | 13973.6674 | inf | 13973.6674 | 13973.6674 | 1.7788e+24 | 6986.8388 | 141.7905 | 95.8952 | 10440.0333 | inf | 10440.0333 | 10440.0333 | 5.8193e+34 | 5220.0166 | 132.5257 | 91.2628 | Diode | 19.142 | 14.3014
Text_H100_Deepspeedds_z3 | 43200 | 11889.3523 | inf | 11889.3523 | 11889.3523 | 1.1861e+24 | 5944.6809 | 145.6615 | 97.8307 | 8826.4647 | inf | 8826.4647 | 8826.4647 | 4.007e+34 | 4413.2324 | 136.3373 | 93.1687 | Diode | 16.2868 | 12.091
Text_H100_Lamma_1B | 43200 | 176263.479 | inf | 176263.479 | 176263.479 | 1.2597e+26 | 88131.7543 | 91.1092 | 70.5546 | 140318.7417 | inf | 140318.7417 | 140318.7417 | 3.1951e+36 | 70159.3708 | 83.6725 | 66.8363 | Diode | 241.4568 | 192.2175
Text_H100_Lamma_3B | 43200 | 34946.3342 | inf | 34946.3342 | 34946.3342 | 5.5574e+24 | 17473.1789 | 121.3645 | 85.6823 | 26707.5632 | inf | 26707.5632 | 26707.5632 | 1.7277e+35 | 13353.7816 | 112.7472 | 81.3736 | Diode | 47.8717 | 36.5857
Text_H100_Lamma_8B | 43200 | 11889.3523 | inf | 11889.3523 | 11889.3523 | 1.1861e+24 | 5944.6809 | 145.6615 | 97.8307 | 8826.4647 | inf | 8826.4647 | 8826.4647 | 4.007e+34 | 4413.2324 | 136.3373 | 93.1687 | Diode | 16.2868 | 12.091
Text_H100_SeqLength_1024 | 43200 | 11941.0933 | inf | 11941.0933 | 11941.0933 | 1.2014e+24 | 5970.5515 | 145.5563 | 97.7781 | 8830.5947 | inf | 8830.5947 | 8830.5947 | 4.0678e+34 | 4415.2973 | 136.3265 | 93.1633 | Diode | 16.3577 | 12.0967
Text_H100_SeqLength_2048 | 43200 | 11889.3523 | inf | 11889.3523 | 11889.3523 | 1.1861e+24 | 5944.6809 | 145.6615 | 97.8307 | 8826.4647 | inf | 8826.4647 | 8826.4647 | 4.007e+34 | 4413.2324 | 136.3373 | 93.1687 | Diode | 16.2868 | 12.091
Text_H100_SeqLength_4096 | 43200 | 12089.0831 | inf | 12089.0831 | 12089.0831 | 1.2099e+24 | 6044.5464 | 145.2583 | 97.6291 | 8991.7534 | inf | 8991.7534 | 8991.7534 | 4.0966e+34 | 4495.8767 | 135.9118 | 92.9559 | Diode | 16.5604 | 12.3175