## All
stage | rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
Proposed_metrics | 1 | P_rms_MW | 64 | 0.9845 | 0 | 0.9315 | 0 | p<0.01 | 1
Proposed_metrics | 2 | P_max_avg_60s_MW | 64 | 0.9245 | 0 | 0.8194 | 0 | p<0.01 | 2.5
Proposed_metrics | 3 | Swing_period60s_mean_MW_x_E_MJ | 64 | 0.9268 | 0 | 0.7976 | 0 | p<0.01 | 3
Proposed_metrics | 4 | P_max_avg_180s_MW | 64 | 0.9176 | 0 | 0.8085 | 0 | p<0.01 | 4
Proposed_metrics | 5 | Swing_period60s_median_MW_x_E_MJ | 64 | 0.922 | 0 | 0.7927 | 0 | p<0.01 | 4.5
Proposed_metrics | 6 | Swing_period60s_max_MW_x_E_MJ | 64 | 0.9143 | 0 | 0.7788 | 0 | p<0.01 | 6
Proposed_metrics | 7 | P_max_avg_300s_MW | 64 | 0.8803 | 0 | 0.753 | 0 | p<0.01 | 8.5
Proposed_metrics | 8 | Swing_period60s_median_MW_x_Prms_MW | 64 | 0.8847 | 0 | 0.7331 | 0 | p<0.01 | 9
Proposed_metrics | 9 | Swing_period60s_mean_MW_x_Prms_MW | 64 | 0.8913 | 0 | 0.7312 | 0 | p<0.01 | 9.5
Proposed_metrics | 10 | P_mean_MW | 64 | 0.856 | 0 | 0.7432 | 0 | p<0.01 | 10
Proposed_metrics | 11 | Swing_period60s_max_MW_x_Prms_MW | 64 | 0.8832 | 0 | 0.7321 | 0 | p<0.01 | 10
Proposed_metrics | 12 | Energy_MWh | 64 | 0.856 | 0 | 0.7432 | 0 | p<0.01 | 10
Proposed_metrics | 13 | Swing_period10s_max_MW_x_E_MJ | 64 | 0.843 | 0 | 0.6855 | 0 | p<0.01 | 13
Proposed_metrics | 14 | Swing_period10s_max_MW_x_Prms_MW | 64 | 0.8356 | 0 | 0.6746 | 0 | p<0.01 | 14
Proposed_metrics | 15 | Swing_period10s_mean_MW_x_E_MJ | 64 | 0.7904 | 0 | 0.6448 | 0 | p<0.01 | 16
Proposed_metrics | 16 | Swing_period5s_max_MW_x_E_MJ | 64 | 0.7951 | 0 | 0.625 | 0 | p<0.01 | 17
Proposed_metrics | 17 | Swing_period5s_max_MW_x_Prms_MW | 64 | 0.7908 | 0 | 0.626 | 0 | p<0.01 | 17
Proposed_metrics | 18 | P_max_MW | 64 | 0.7802 | 0 | 0.6296 | 0 | p<0.01 | 18
Proposed_metrics | 19 | Swing_period1s_max_MW_x_Prms_MW | 64 | 0.7792 | 0 | 0.628 | 0 | p<0.01 | 19
Proposed_metrics | 20 | Max_change_in_1s_MW | 64 | 0.7848 | 0 | 0.6101 | 0 | p<0.01 | 20.5
Proposed_metrics | 21 | Swing_period10s_mean_MW_x_Prms_MW | 64 | 0.7779 | 0 | 0.622 | 0 | p<0.01 | 21.5
Proposed_metrics | 22 | Max_change_in_60s_MW | 64 | 0.7823 | 0 | 0.6002 | 0 | p<0.01 | 22.25
Proposed_metrics | 23 | Swing_period1s_max_MW_x_E_MJ | 64 | 0.7765 | 0 | 0.623 | 0 | p<0.01 | 22.5
Proposed_metrics | 24 | P_p999_MW | 64 | 0.7731 | 0 | 0.619 | 0 | p<0.01 | 25
Proposed_metrics | 25 | Swing_period5s_max_MW | 64 | 0.7777 | 0 | 0.5982 | 0 | p<0.01 | 25.5
Proposed_metrics | 26 | Power_cycle_dP_max_MW | 64 | 0.7776 | 0 | 0.5982 | 0 | p<0.01 | 26
Proposed_metrics | 27 | Swing_period1s_max_MW | 64 | 0.7755 | 0 | 0.5982 | 0 | p<0.01 | 27
Proposed_metrics | 28 | Swing_period10s_max_MW | 64 | 0.7739 | 0 | 0.5903 | 0 | p<0.01 | 29
Proposed_metrics | 29 | Damage_proxy_per_h | 64 | 0.768 | 0 | 0.5913 | 0 | p<0.01 | 29.5
Proposed_metrics | 30 | Swing_period10s_median_MW_x_E_MJ | 64 | 0.7169 | 0 | 0.6042 | 0 | p<0.01 | 32
Proposed_metrics | 31 | Swing_p95_p05_MW | 64 | 0.756 | 0 | 0.5863 | 0 | p<0.01 | 32
Proposed_metrics | 32 | Swing_period10s_median_MW_x_Prms_MW | 64 | 0.7172 | 0 | 0.6002 | 0 | p<0.01 | 32.25
Proposed_metrics | 33 | Power_cycles_ge_50pct_per_h | 64 | 0.7465 | 0 | 0.5884 | 0 | p<0.01 | 33
Proposed_metrics | 34 | Swing_period60s_mean_MW | 64 | 0.7608 | 0 | 0.5744 | 0 | p<0.01 | 33
Proposed_metrics | 35 | Swing_period60s_max_MW | 64 | 0.7495 | 0 | 0.5724 | 0 | p<0.01 | 34.5
Proposed_metrics | 36 | Swing_filtered_tau0.26s_MW | 64 | 0.7375 | 0 | 0.5754 | 0 | p<0.01 | 35
Proposed_metrics | 37 | Swing_period60s_median_MW | 64 | 0.7485 | 0 | 0.5694 | 0 | p<0.01 | 35.5
Proposed_metrics | 38 | P_high_level_MW | 64 | 0.7212 | 0 | 0.5833 | 0 | p<0.01 | 36
Proposed_metrics | 39 | Ramp_p99_MW_per_s | 64 | 0.7349 | 0 | 0.5625 | 0 | p<0.01 | 37.5
Proposed_metrics | 40 | Swing_avg_1s_MW | 64 | 0.7243 | 0 | 0.5516 | 0 | p<0.01 | 39.5
Proposed_metrics | 41 | Step_height_pct_rating | 64 | 0.7083 | 0 | 0.5575 | 0 | p<0.01 | 41
Proposed_metrics | 42 | Step_height_MW | 64 | 0.7083 | 0 | 0.5575 | 0 | p<0.01 | 41
Proposed_metrics | 43 | Swing_period5s_mean_MW_x_E_MJ | 64 | 0.7065 | 0 | 0.5327 | 0 | p<0.01 | 43
Proposed_metrics | 44 | Swing_period5s_mean_MW_x_Prms_MW | 64 | 0.6959 | 0 | 0.5258 | 0 | p<0.01 | 44
Proposed_metrics | 45 | Swing_period1s_mean_MW_x_E_MJ | 64 | 0.6782 | 0 | 0.5069 | 0 | p<0.01 | 45.75
Proposed_metrics | 46 | Swing_period1s_mean_MW_x_Prms_MW | 64 | 0.6776 | 0 | 0.5069 | 0 | p<0.01 | 46.25
Proposed_metrics | 47 | Swing_period10s_median_MW | 64 | 0.6413 | 0 | 0.5079 | 0 | p<0.01 | 46.5
Proposed_metrics | 48 | Swing_period10s_mean_MW | 64 | 0.658 | 0 | 0.5 | 0 | p<0.01 | 47.5
Proposed_metrics | 49 | Swing_period5s_mean_MW | 64 | 0.5593 | 0 | 0.4067 | 0 | p<0.01 | 49.5
Proposed_metrics | 50 | Swing_period1s_mean_MW | 64 | 0.5439 | 0 | 0.3929 | 0 | p<0.01 | 50.5
Proposed_metrics | 51 | Swing_period5s_median_MW_x_E_MJ | 64 | 0.5305 | 0 | 0.4097 | 0 | p<0.01 | 50.5
Proposed_metrics | 52 | P_low_level_MW | 64 | 0.5356 | 0 | 0.376 | 0 | p<0.01 | 52
Proposed_metrics | 53 | Swing_period5s_median_MW_x_Prms_MW | 64 | 0.4957 | 0 | 0.3819 | 0 | p<0.01 | 52.5
Proposed_metrics | 54 | Swing_period1s_median_MW_x_E_MJ | 64 | 0.4948 | 0 | 0.37 | 0 | p<0.01 | 54.25
Proposed_metrics | 55 | Swing_period1s_median_MW_x_Prms_MW | 64 | 0.4936 | 0 | 0.37 | 0 | p<0.01 | 54.75
Proposed_metrics | 56 | P_min_MW | 64 | 0.4739 | 0.0001 | 0.3115 | 0.0003 | p<0.01 | 56
Proposed_metrics | 57 | Swing_filtered_tau3.31s_MW | 64 | 0.4208 | 0.0005 | 0.3026 | 0.0004 | p<0.01 | 57
Proposed_metrics | 58 | Swing_period5s_median_MW | 64 | 0.4161 | 0.0006 | 0.3006 | 0.0004 | p<0.01 | 58
Proposed_metrics | 59 | Swing_period1s_median_MW | 64 | 0.4065 | 0.0009 | 0.2966 | 0.0005 | p<0.01 | 59
Proposed_metrics | 60 | Power_cycles_ge_30pct_per_h | 64 | 0.3657 | 0.003 | 0.2558 | 0.0031 | p<0.01 | 60
Proposed_metrics | 61 | Power_cycles_ge_10pct_per_h | 64 | 0.3632 | 0.0032 | 0.2393 | 0.0054 | p<0.01 | 61
Proposed_metrics | 62 | Dwell_low_p95_s | 64 | -0.2888 | 0.0206 | -0.2048 | 0.018 | p<0.05 | 62
Proposed_metrics | 63 | Swing_filtered_tau159s_MW | 64 | 0.2722 | 0.0296 | 0.1895 | 0.0269 | p<0.05 | 63
Proposed_metrics | 64 | Dwell_low_mean_s | 64 | -0.2565 | 0.0408 | -0.154 | 0.0742 | - | 64
Proposed_metrics | 65 | Transitions_per_h | 64 | 0.2209 | 0.0794 | 0.1493 | 0.084 | - | 66
Proposed_metrics | 66 | Burst_period_mean_s | 64 | -0.2203 | 0.0802 | -0.15 | 0.082 | - | 66
Proposed_metrics | 67 | Bursts_per_h | 64 | 0.2209 | 0.0794 | 0.1493 | 0.084 | - | 66
Proposed_metrics | 68 | Dominant_period_s | 64 | -0.201 | 0.1112 | -0.1417 | 0.1019 | - | 68
Proposed_metrics | 69 | Burst_period_CV | 64 | 0.1281 | 0.3132 | 0.088 | 0.3076 | - | 69
Proposed_metrics | 70 | Time_at_high_load_pct | 64 | 0.1261 | 0.3206 | 0.044 | 0.61 | - | 70
Proposed_metrics | 71 | Peak_to_mean | 64 | -0.1026 | 0.4196 | -0.0174 | 0.8393 | - | 71
Proposed_metrics | 72 | Dwell_high_p95_s | 64 | 0.0315 | 0.8048 | 0.008 | 0.9261 | - | 72
Proposed_metrics | 73 | Dwell_high_mean_s | 64 | 0.0288 | 0.8215 | 0.006 | 0.9445 | - | 73
Grid_operator_metrics | 1 | Peak_demand_15min_MW | 64 | 0.856 | 0 | 0.7432 | 0 | p<0.01 | 1
Grid_operator_metrics | 2 | Max_change_in_5s_MW | 64 | 0.7851 | 0 | 0.5992 | 0 | p<0.01 | 2
Grid_operator_metrics | 3 | SoCo_band_0.1_0.5Hz_amp_60s_MW | 64 | 0.7471 | 0 | 0.5804 | 0 | p<0.01 | 3
Grid_operator_metrics | 4 | Flicker_Pst_max_SCR20 | 64 | 0.6863 | 0 | 0.5238 | 0 | p<0.01 | 4
Grid_operator_metrics | 5 | SoCo_band_0.5_0.8Hz_amp_60s_MW | 64 | 0.6104 | 0 | 0.4425 | 0 | p<0.01 | 5
Grid_operator_metrics | 6 | Swing_avg_4s_MW | 64 | 0.451 | 0.0002 | 0.3165 | 0.0002 | p<0.01 | 6
Grid_operator_metrics | 7 | Variability_1min_std_MW | 64 | 0.342 | 0.0057 | 0.2421 | 0.0047 | p<0.01 | 7
Grid_operator_metrics | 8 | Swing_avg_60s_MW | 64 | 0.3103 | 0.0126 | 0.2113 | 0.0136 | p<0.05 | 8
Grid_operator_metrics | 9 | SoCo_band_0.8_2Hz_amp_60s_MW | 64 | 0.2823 | 0.0238 | 0.2004 | 0.0193 | p<0.05 | 9.5
Grid_operator_metrics | 10 | Ramp_max_MW_per_min | 64 | 0.2857 | 0.0221 | 0.1944 | 0.0231 | p<0.05 | 10
Grid_operator_metrics | 11 | Max_change_in_0.1s_MW | 64 | 0.2794 | 0.0254 | 0.1964 | 0.0218 | p<0.05 | 10.5
Grid_operator_metrics | 12 | Swing_avg_300s_MW | 64 | 0.2788 | 0.0257 | 0.1905 | 0.0261 | p<0.05 | 12.5
Grid_operator_metrics | 13 | ERCOT_changes_gt25pct_in_5s_per_h | 64 | 0.2733 | 0.0289 | 0.1924 | 0.0263 | p<0.05 | 12.5
Grid_operator_metrics | 14 | LIPA_band_5_23.75Hz_amp_10s_MW | 64 | 0.2122 | 0.0923 | 0.1508 | 0.0782 | - | 14
Electrical | 1 | I_IGBT_rms_A | 64 | 0.9845 | 0 | 0.9315 | 0 | p<0.01 | 1
Electrical | 2 | P_loss_IGBT_mean_W | 64 | 0.9811 | 0 | 0.9296 | 0 | p<0.01 | 2
Electrical | 3 | P_loss_IGBT_swing_W | 64 | 0.7596 | 0 | 0.5952 | 0 | p<0.01 | 3
Thermal | 1 | IGBT_burst_Tmean_C | 61 | 0.9741 | 0 | 0.918 | 0 | p<0.01 | 1
Thermal | 2 | IGBT_burst_dT_eq_K | 61 | 0.7009 | 0 | 0.5519 | 0 | p<0.01 | 2
Thermal | 3 | IGBT_burst_duration_mean_s | 61 | -0.2525 | 0.0496 | -0.1809 | 0.0394 | p<0.05 | 3

## Proposed_metrics
rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
1 | P_rms_MW | 64 | 0.9845 | 0 | 0.9315 | 0 | p<0.01 | 1
2 | P_max_avg_60s_MW | 64 | 0.9245 | 0 | 0.8194 | 0 | p<0.01 | 2.5
3 | Swing_period60s_mean_MW_x_E_MJ | 64 | 0.9268 | 0 | 0.7976 | 0 | p<0.01 | 3
4 | P_max_avg_180s_MW | 64 | 0.9176 | 0 | 0.8085 | 0 | p<0.01 | 4
5 | Swing_period60s_median_MW_x_E_MJ | 64 | 0.922 | 0 | 0.7927 | 0 | p<0.01 | 4.5
6 | Swing_period60s_max_MW_x_E_MJ | 64 | 0.9143 | 0 | 0.7788 | 0 | p<0.01 | 6
7 | P_max_avg_300s_MW | 64 | 0.8803 | 0 | 0.753 | 0 | p<0.01 | 8.5
8 | Swing_period60s_median_MW_x_Prms_MW | 64 | 0.8847 | 0 | 0.7331 | 0 | p<0.01 | 9
9 | Swing_period60s_mean_MW_x_Prms_MW | 64 | 0.8913 | 0 | 0.7312 | 0 | p<0.01 | 9.5
10 | P_mean_MW | 64 | 0.856 | 0 | 0.7432 | 0 | p<0.01 | 10
11 | Swing_period60s_max_MW_x_Prms_MW | 64 | 0.8832 | 0 | 0.7321 | 0 | p<0.01 | 10
12 | Energy_MWh | 64 | 0.856 | 0 | 0.7432 | 0 | p<0.01 | 10
13 | Swing_period10s_max_MW_x_E_MJ | 64 | 0.843 | 0 | 0.6855 | 0 | p<0.01 | 13
14 | Swing_period10s_max_MW_x_Prms_MW | 64 | 0.8356 | 0 | 0.6746 | 0 | p<0.01 | 14
15 | Swing_period10s_mean_MW_x_E_MJ | 64 | 0.7904 | 0 | 0.6448 | 0 | p<0.01 | 16
16 | Swing_period5s_max_MW_x_E_MJ | 64 | 0.7951 | 0 | 0.625 | 0 | p<0.01 | 17
17 | Swing_period5s_max_MW_x_Prms_MW | 64 | 0.7908 | 0 | 0.626 | 0 | p<0.01 | 17
18 | P_max_MW | 64 | 0.7802 | 0 | 0.6296 | 0 | p<0.01 | 18
19 | Swing_period1s_max_MW_x_Prms_MW | 64 | 0.7792 | 0 | 0.628 | 0 | p<0.01 | 19
20 | Max_change_in_1s_MW | 64 | 0.7848 | 0 | 0.6101 | 0 | p<0.01 | 20.5
21 | Swing_period10s_mean_MW_x_Prms_MW | 64 | 0.7779 | 0 | 0.622 | 0 | p<0.01 | 21.5
22 | Max_change_in_60s_MW | 64 | 0.7823 | 0 | 0.6002 | 0 | p<0.01 | 22.25
23 | Swing_period1s_max_MW_x_E_MJ | 64 | 0.7765 | 0 | 0.623 | 0 | p<0.01 | 22.5
24 | P_p999_MW | 64 | 0.7731 | 0 | 0.619 | 0 | p<0.01 | 25
25 | Swing_period5s_max_MW | 64 | 0.7777 | 0 | 0.5982 | 0 | p<0.01 | 25.5
26 | Power_cycle_dP_max_MW | 64 | 0.7776 | 0 | 0.5982 | 0 | p<0.01 | 26
27 | Swing_period1s_max_MW | 64 | 0.7755 | 0 | 0.5982 | 0 | p<0.01 | 27
28 | Swing_period10s_max_MW | 64 | 0.7739 | 0 | 0.5903 | 0 | p<0.01 | 29
29 | Damage_proxy_per_h | 64 | 0.768 | 0 | 0.5913 | 0 | p<0.01 | 29.5
30 | Swing_period10s_median_MW_x_E_MJ | 64 | 0.7169 | 0 | 0.6042 | 0 | p<0.01 | 32
31 | Swing_p95_p05_MW | 64 | 0.756 | 0 | 0.5863 | 0 | p<0.01 | 32
32 | Swing_period10s_median_MW_x_Prms_MW | 64 | 0.7172 | 0 | 0.6002 | 0 | p<0.01 | 32.25
33 | Power_cycles_ge_50pct_per_h | 64 | 0.7465 | 0 | 0.5884 | 0 | p<0.01 | 33
34 | Swing_period60s_mean_MW | 64 | 0.7608 | 0 | 0.5744 | 0 | p<0.01 | 33
35 | Swing_period60s_max_MW | 64 | 0.7495 | 0 | 0.5724 | 0 | p<0.01 | 34.5
36 | Swing_filtered_tau0.26s_MW | 64 | 0.7375 | 0 | 0.5754 | 0 | p<0.01 | 35
37 | Swing_period60s_median_MW | 64 | 0.7485 | 0 | 0.5694 | 0 | p<0.01 | 35.5
38 | P_high_level_MW | 64 | 0.7212 | 0 | 0.5833 | 0 | p<0.01 | 36
39 | Ramp_p99_MW_per_s | 64 | 0.7349 | 0 | 0.5625 | 0 | p<0.01 | 37.5
40 | Swing_avg_1s_MW | 64 | 0.7243 | 0 | 0.5516 | 0 | p<0.01 | 39.5
41 | Step_height_pct_rating | 64 | 0.7083 | 0 | 0.5575 | 0 | p<0.01 | 41
42 | Step_height_MW | 64 | 0.7083 | 0 | 0.5575 | 0 | p<0.01 | 41
43 | Swing_period5s_mean_MW_x_E_MJ | 64 | 0.7065 | 0 | 0.5327 | 0 | p<0.01 | 43
44 | Swing_period5s_mean_MW_x_Prms_MW | 64 | 0.6959 | 0 | 0.5258 | 0 | p<0.01 | 44
45 | Swing_period1s_mean_MW_x_E_MJ | 64 | 0.6782 | 0 | 0.5069 | 0 | p<0.01 | 45.75
46 | Swing_period1s_mean_MW_x_Prms_MW | 64 | 0.6776 | 0 | 0.5069 | 0 | p<0.01 | 46.25
47 | Swing_period10s_median_MW | 64 | 0.6413 | 0 | 0.5079 | 0 | p<0.01 | 46.5
48 | Swing_period10s_mean_MW | 64 | 0.658 | 0 | 0.5 | 0 | p<0.01 | 47.5
49 | Swing_period5s_mean_MW | 64 | 0.5593 | 0 | 0.4067 | 0 | p<0.01 | 49.5
50 | Swing_period1s_mean_MW | 64 | 0.5439 | 0 | 0.3929 | 0 | p<0.01 | 50.5
51 | Swing_period5s_median_MW_x_E_MJ | 64 | 0.5305 | 0 | 0.4097 | 0 | p<0.01 | 50.5
52 | P_low_level_MW | 64 | 0.5356 | 0 | 0.376 | 0 | p<0.01 | 52
53 | Swing_period5s_median_MW_x_Prms_MW | 64 | 0.4957 | 0 | 0.3819 | 0 | p<0.01 | 52.5
54 | Swing_period1s_median_MW_x_E_MJ | 64 | 0.4948 | 0 | 0.37 | 0 | p<0.01 | 54.25
55 | Swing_period1s_median_MW_x_Prms_MW | 64 | 0.4936 | 0 | 0.37 | 0 | p<0.01 | 54.75
56 | P_min_MW | 64 | 0.4739 | 0.0001 | 0.3115 | 0.0003 | p<0.01 | 56
57 | Swing_filtered_tau3.31s_MW | 64 | 0.4208 | 0.0005 | 0.3026 | 0.0004 | p<0.01 | 57
58 | Swing_period5s_median_MW | 64 | 0.4161 | 0.0006 | 0.3006 | 0.0004 | p<0.01 | 58
59 | Swing_period1s_median_MW | 64 | 0.4065 | 0.0009 | 0.2966 | 0.0005 | p<0.01 | 59
60 | Power_cycles_ge_30pct_per_h | 64 | 0.3657 | 0.003 | 0.2558 | 0.0031 | p<0.01 | 60
61 | Power_cycles_ge_10pct_per_h | 64 | 0.3632 | 0.0032 | 0.2393 | 0.0054 | p<0.01 | 61
62 | Dwell_low_p95_s | 64 | -0.2888 | 0.0206 | -0.2048 | 0.018 | p<0.05 | 62
63 | Swing_filtered_tau159s_MW | 64 | 0.2722 | 0.0296 | 0.1895 | 0.0269 | p<0.05 | 63
64 | Dwell_low_mean_s | 64 | -0.2565 | 0.0408 | -0.154 | 0.0742 | - | 64
65 | Transitions_per_h | 64 | 0.2209 | 0.0794 | 0.1493 | 0.084 | - | 66
66 | Burst_period_mean_s | 64 | -0.2203 | 0.0802 | -0.15 | 0.082 | - | 66
67 | Bursts_per_h | 64 | 0.2209 | 0.0794 | 0.1493 | 0.084 | - | 66
68 | Dominant_period_s | 64 | -0.201 | 0.1112 | -0.1417 | 0.1019 | - | 68
69 | Burst_period_CV | 64 | 0.1281 | 0.3132 | 0.088 | 0.3076 | - | 69
70 | Time_at_high_load_pct | 64 | 0.1261 | 0.3206 | 0.044 | 0.61 | - | 70
71 | Peak_to_mean | 64 | -0.1026 | 0.4196 | -0.0174 | 0.8393 | - | 71
72 | Dwell_high_p95_s | 64 | 0.0315 | 0.8048 | 0.008 | 0.9261 | - | 72
73 | Dwell_high_mean_s | 64 | 0.0288 | 0.8215 | 0.006 | 0.9445 | - | 73

## Grid_operator_metrics
rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
1 | Peak_demand_15min_MW | 64 | 0.856 | 0 | 0.7432 | 0 | p<0.01 | 1
2 | Max_change_in_5s_MW | 64 | 0.7851 | 0 | 0.5992 | 0 | p<0.01 | 2
3 | SoCo_band_0.1_0.5Hz_amp_60s_MW | 64 | 0.7471 | 0 | 0.5804 | 0 | p<0.01 | 3
4 | Flicker_Pst_max_SCR20 | 64 | 0.6863 | 0 | 0.5238 | 0 | p<0.01 | 4
5 | SoCo_band_0.5_0.8Hz_amp_60s_MW | 64 | 0.6104 | 0 | 0.4425 | 0 | p<0.01 | 5
6 | Swing_avg_4s_MW | 64 | 0.451 | 0.0002 | 0.3165 | 0.0002 | p<0.01 | 6
7 | Variability_1min_std_MW | 64 | 0.342 | 0.0057 | 0.2421 | 0.0047 | p<0.01 | 7
8 | Swing_avg_60s_MW | 64 | 0.3103 | 0.0126 | 0.2113 | 0.0136 | p<0.05 | 8
9 | SoCo_band_0.8_2Hz_amp_60s_MW | 64 | 0.2823 | 0.0238 | 0.2004 | 0.0193 | p<0.05 | 9.5
10 | Ramp_max_MW_per_min | 64 | 0.2857 | 0.0221 | 0.1944 | 0.0231 | p<0.05 | 10
11 | Max_change_in_0.1s_MW | 64 | 0.2794 | 0.0254 | 0.1964 | 0.0218 | p<0.05 | 10.5
12 | Swing_avg_300s_MW | 64 | 0.2788 | 0.0257 | 0.1905 | 0.0261 | p<0.05 | 12.5
13 | ERCOT_changes_gt25pct_in_5s_per_h | 64 | 0.2733 | 0.0289 | 0.1924 | 0.0263 | p<0.05 | 12.5
14 | LIPA_band_5_23.75Hz_amp_10s_MW | 64 | 0.2122 | 0.0923 | 0.1508 | 0.0782 | - | 14

## Electrical_characteristics
rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
1 | I_IGBT_rms_A | 64 | 0.9845 | 0 | 0.9315 | 0 | p<0.01 | 1
2 | P_loss_IGBT_mean_W | 64 | 0.9811 | 0 | 0.9296 | 0 | p<0.01 | 2
3 | P_loss_IGBT_swing_W | 64 | 0.7596 | 0 | 0.5952 | 0 | p<0.01 | 3

## Thermal_characteristics
rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
1 | IGBT_burst_Tmean_C | 61 | 0.9741 | 0 | 0.918 | 0 | p<0.01 | 1
2 | IGBT_burst_dT_eq_K | 61 | 0.7009 | 0 | 0.5519 | 0 | p<0.01 | 2
3 | IGBT_burst_duration_mean_s | 61 | -0.2525 | 0.0496 | -0.1809 | 0.0394 | p<0.05 | 3