## All
stage | rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
Proposed_metrics | 1 | P_rms_MW | 32 | 0.9751 | 0 | 0.9153 | 0 | p<0.01 | 1
Proposed_metrics | 2 | Swing_period60s_median_MW_x_E_MJ | 32 | 0.9249 | 0 | 0.8347 | 0 | p<0.01 | 2
Proposed_metrics | 3 | Swing_period60s_max_MW_x_E_MJ | 32 | 0.9179 | 0 | 0.8226 | 0 | p<0.01 | 3
Proposed_metrics | 4 | Swing_period60s_mean_MW_x_E_MJ | 32 | 0.9124 | 0 | 0.8065 | 0 | p<0.01 | 4
Proposed_metrics | 5 | Swing_period60s_median_MW_x_Prms_MW | 32 | 0.893 | 0 | 0.7863 | 0 | p<0.01 | 5
Proposed_metrics | 6 | Swing_period60s_mean_MW_x_Prms_MW | 32 | 0.8823 | 0 | 0.7419 | 0 | p<0.01 | 6.5
Proposed_metrics | 7 | Swing_period60s_max_MW_x_Prms_MW | 32 | 0.882 | 0 | 0.7661 | 0 | p<0.01 | 6.5
Proposed_metrics | 8 | Swing_period10s_max_MW_x_E_MJ | 32 | 0.8666 | 0 | 0.7137 | 0 | p<0.01 | 8.5
Proposed_metrics | 9 | P_max_avg_60s_MW | 32 | 0.8519 | 0 | 0.7097 | 0 | p<0.01 | 9.5
Proposed_metrics | 10 | P_max_avg_180s_MW | 32 | 0.8468 | 0 | 0.7258 | 0 | p<0.01 | 9.5
Proposed_metrics | 11 | Swing_period10s_max_MW_x_Prms_MW | 32 | 0.8482 | 0 | 0.6895 | 0 | p<0.01 | 10.5
Proposed_metrics | 12 | Swing_period1s_max_MW | 32 | 0.8068 | 0 | 0.6815 | 0 | p<0.01 | 13.5
Proposed_metrics | 13 | Swing_period5s_max_MW | 32 | 0.8123 | 0 | 0.6694 | 0 | p<0.01 | 14.25
Proposed_metrics | 14 | P_mean_MW | 32 | 0.8051 | 0 | 0.6799 | 0 | p<0.01 | 15
Proposed_metrics | 15 | Energy_MWh | 32 | 0.8051 | 0 | 0.6799 | 0 | p<0.01 | 15
Proposed_metrics | 16 | Power_cycle_dP_max_MW | 32 | 0.8116 | 0 | 0.6613 | 0 | p<0.01 | 16
Proposed_metrics | 17 | Max_change_in_60s_MW | 32 | 0.8094 | 0 | 0.6532 | 0 | p<0.01 | 17
Proposed_metrics | 18 | Swing_period1s_max_MW_x_Prms_MW | 32 | 0.8021 | 0 | 0.6694 | 0 | p<0.01 | 17.25
Proposed_metrics | 19 | Max_change_in_1s_MW | 32 | 0.7988 | 0 | 0.6734 | 0 | p<0.01 | 18
Proposed_metrics | 20 | P_max_avg_300s_MW | 32 | 0.8017 | 0 | 0.6653 | 0 | p<0.01 | 18.5
Proposed_metrics | 21 | Swing_period1s_max_MW_x_E_MJ | 32 | 0.7966 | 0 | 0.6492 | 0 | p<0.01 | 21.75
Proposed_metrics | 22 | Damage_proxy_per_h | 32 | 0.7944 | 0 | 0.6492 | 0 | p<0.01 | 22.25
Proposed_metrics | 23 | Swing_period10s_max_MW | 32 | 0.8006 | 0 | 0.6371 | 0 | p<0.01 | 22.75
Proposed_metrics | 24 | P_max_MW | 32 | 0.7929 | 0 | 0.6452 | 0 | p<0.01 | 23.5
Proposed_metrics | 25 | Swing_p95_p05_MW | 32 | 0.7808 | 0 | 0.6411 | 0 | p<0.01 | 25
Proposed_metrics | 26 | P_p999_MW | 32 | 0.7918 | 0 | 0.6371 | 0 | p<0.01 | 25.25
Proposed_metrics | 27 | Swing_period5s_max_MW_x_Prms_MW | 32 | 0.7731 | 0 | 0.6169 | 0 | p<0.01 | 27.5
Proposed_metrics | 28 | Swing_period5s_max_MW_x_E_MJ | 32 | 0.7768 | 0 | 0.6089 | 0 | p<0.01 | 28.5
Proposed_metrics | 29 | Swing_period60s_median_MW | 32 | 0.7698 | 0 | 0.6129 | 0 | p<0.01 | 28.75
Proposed_metrics | 30 | Swing_period60s_max_MW | 32 | 0.7665 | 0 | 0.6129 | 0 | p<0.01 | 29.25
Proposed_metrics | 31 | Swing_filtered_tau0.26s_MW | 32 | 0.7632 | 0 | 0.6048 | 0 | p<0.01 | 31
Proposed_metrics | 32 | Swing_avg_1s_MW | 32 | 0.7573 | 0 | 0.5927 | 0 | p<0.01 | 33
Proposed_metrics | 33 | P_high_level_MW | 32 | 0.7405 | 0 | 0.6008 | 0 | p<0.01 | 33
Proposed_metrics | 34 | Swing_period60s_mean_MW | 32 | 0.7522 | 0 | 0.5927 | 0 | p<0.01 | 33.5
Proposed_metrics | 35 | Swing_period10s_mean_MW_x_E_MJ | 32 | 0.7111 | 0 | 0.5927 | 0 | p<0.01 | 36
Proposed_metrics | 36 | Step_height_pct_rating | 32 | 0.7185 | 0 | 0.5766 | 0 | p<0.01 | 37
Proposed_metrics | 37 | Step_height_MW | 32 | 0.7185 | 0 | 0.5766 | 0 | p<0.01 | 37
Proposed_metrics | 38 | Power_cycles_ge_50pct_per_h | 32 | 0.7329 | 0 | 0.5742 | 0 | p<0.01 | 37
Proposed_metrics | 39 | Swing_period10s_median_MW_x_E_MJ | 32 | 0.6716 | 0 | 0.5847 | 0 | p<0.01 | 38.5
Proposed_metrics | 40 | Swing_period10s_mean_MW_x_Prms_MW | 32 | 0.6888 | 0 | 0.5645 | 0 | p<0.01 | 40
Proposed_metrics | 41 | P_low_level_MW | 32 | 0.6965 | 0 | 0.504 | 0 | p<0.01 | 41
Proposed_metrics | 42 | Ramp_p99_MW_per_s | 32 | 0.6686 | 0 | 0.504 | 0 | p<0.01 | 42.5
Proposed_metrics | 43 | Swing_period10s_median_MW_x_Prms_MW | 32 | 0.6411 | 0.0001 | 0.5363 | 0 | p<0.01 | 43
Proposed_metrics | 44 | Swing_period5s_mean_MW_x_E_MJ | 32 | 0.6642 | 0 | 0.504 | 0 | p<0.01 | 43
Proposed_metrics | 45 | Swing_period5s_mean_MW_x_Prms_MW | 32 | 0.6433 | 0.0001 | 0.4839 | 0.0001 | p<0.01 | 44.75
Proposed_metrics | 46 | Swing_period10s_mean_MW | 32 | 0.6162 | 0.0002 | 0.4758 | 0.0001 | p<0.01 | 46.5
Proposed_metrics | 47 | Swing_period5s_median_MW_x_E_MJ | 32 | 0.5568 | 0.0009 | 0.4839 | 0.0001 | p<0.01 | 48.25
Proposed_metrics | 48 | Swing_period10s_median_MW | 32 | 0.5898 | 0.0004 | 0.4718 | 0.0001 | p<0.01 | 48.5
Proposed_metrics | 49 | Swing_period1s_mean_MW_x_Prms_MW | 32 | 0.6004 | 0.0003 | 0.4395 | 0.0003 | p<0.01 | 49
Proposed_metrics | 50 | Swing_period1s_mean_MW_x_E_MJ | 32 | 0.6004 | 0.0003 | 0.4395 | 0.0003 | p<0.01 | 49
Proposed_metrics | 51 | Swing_period5s_median_MW_x_Prms_MW | 32 | 0.5466 | 0.0012 | 0.4597 | 0.0001 | p<0.01 | 50.5
Proposed_metrics | 52 | P_min_MW | 32 | 0.5817 | 0.0005 | 0.371 | 0.0025 | p<0.01 | 52
Proposed_metrics | 53 | Swing_period5s_mean_MW | 32 | 0.5458 | 0.0012 | 0.3911 | 0.0014 | p<0.01 | 52.75
Proposed_metrics | 54 | Swing_period5s_median_MW | 32 | 0.4956 | 0.0039 | 0.3911 | 0.0014 | p<0.01 | 53.75
Proposed_metrics | 55 | Swing_filtered_tau3.31s_MW | 32 | 0.4978 | 0.0037 | 0.3427 | 0.0055 | p<0.01 | 55.5
Proposed_metrics | 56 | Swing_period1s_mean_MW | 32 | 0.4938 | 0.0041 | 0.3508 | 0.0044 | p<0.01 | 55.5
Proposed_metrics | 57 | Swing_period1s_median_MW_x_E_MJ | 32 | 0.4751 | 0.006 | 0.3427 | 0.0055 | p<0.01 | 57
Proposed_metrics | 58 | Swing_period1s_median_MW_x_Prms_MW | 32 | 0.4703 | 0.0066 | 0.3427 | 0.0055 | p<0.01 | 57.5
Proposed_metrics | 59 | Swing_filtered_tau159s_MW | 32 | 0.4337 | 0.0132 | 0.3105 | 0.0123 | p<0.05 | 59
Proposed_metrics | 60 | Swing_period1s_median_MW | 32 | 0.335 | 0.0609 | 0.2419 | 0.0531 | - | 60
Proposed_metrics | 61 | Power_cycles_ge_10pct_per_h | 32 | 0.326 | 0.0686 | 0.2141 | 0.0882 | - | 61
Proposed_metrics | 62 | Power_cycles_ge_30pct_per_h | 32 | 0.3209 | 0.0734 | 0.2118 | 0.0937 | - | 62
Proposed_metrics | 63 | Burst_period_CV | 32 | 0.2548 | 0.1594 | 0.1845 | 0.1436 | - | 63
Proposed_metrics | 64 | Bursts_per_h | 32 | 0.2168 | 0.2334 | 0.1482 | 0.2416 | - | 65
Proposed_metrics | 65 | Transitions_per_h | 32 | 0.2168 | 0.2334 | 0.1482 | 0.2416 | - | 65
Proposed_metrics | 66 | Burst_period_mean_s | 32 | -0.2166 | 0.2338 | -0.1517 | 0.2292 | - | 65
Proposed_metrics | 67 | Dwell_low_p95_s | 32 | -0.2096 | 0.2497 | -0.1405 | 0.2683 | - | 67
Proposed_metrics | 68 | Dwell_low_mean_s | 32 | -0.1946 | 0.2859 | -0.1353 | 0.2835 | - | 68
Proposed_metrics | 69 | Dominant_period_s | 32 | -0.187 | 0.3055 | -0.1317 | 0.2979 | - | 69
Proposed_metrics | 70 | Dwell_high_p95_s | 32 | 0.1138 | 0.5351 | 0.0697 | 0.5806 | - | 70
Proposed_metrics | 71 | Dwell_high_mean_s | 32 | 0.1116 | 0.5431 | 0.0615 | 0.6259 | - | 71
Proposed_metrics | 72 | Time_at_high_load_pct | 32 | 0.0815 | 0.6575 | 0.0205 | 0.8709 | - | 72
Proposed_metrics | 73 | Peak_to_mean | 32 | -0.0326 | 0.8592 | 0.0142 | 0.9095 | - | 73
Grid_operator_metrics | 1 | Max_change_in_5s_MW | 32 | 0.8079 | 0 | 0.6452 | 0 | p<0.01 | 1
Grid_operator_metrics | 2 | SoCo_band_0.1_0.5Hz_amp_60s_MW | 32 | 0.6298 | 0.0001 | 0.4839 | 0.0001 | p<0.01 | 2
Grid_operator_metrics | 3 | SoCo_band_0.5_0.8Hz_amp_60s_MW | 32 | 0.5499 | 0.0011 | 0.379 | 0.002 | p<0.01 | 3
Grid_operator_metrics | 4 | Swing_avg_4s_MW | 32 | 0.5422 | 0.0013 | 0.3347 | 0.0067 | p<0.01 | 4
Grid_operator_metrics | 5 | Swing_avg_300s_MW | 32 | 0.4238 | 0.0157 | 0.3306 | 0.0075 | p<0.05 | 5
Grid_operator_metrics | 6 | Swing_avg_60s_MW | 32 | 0.4128 | 0.0189 | 0.3105 | 0.0123 | p<0.05 | 6
Grid_operator_metrics | 7 | Ramp_max_MW_per_min | 32 | 0.4054 | 0.0213 | 0.3024 | 0.0148 | p<0.05 | 7
Grid_operator_metrics | 8 | Max_change_in_0.1s_MW | 32 | 0.3739 | 0.035 | 0.2702 | 0.0302 | p<0.05 | 8
Grid_operator_metrics | 9 | SoCo_band_0.8_2Hz_amp_60s_MW | 32 | 0.3361 | 0.06 | 0.2419 | 0.0531 | - | 9
Grid_operator_metrics | 10 | LIPA_band_5_23.75Hz_amp_10s_MW | 32 | 0.3185 | 0.0756 | 0.2258 | 0.0716 | - | 10
Grid_operator_metrics | 11 | ERCOT_changes_gt25pct_in_5s_per_h | 32 | 0.2143 | 0.2388 | 0.159 | 0.21 | - | 11
Electrical | 1 | I_IGBT_rms_A | 32 | 0.9751 | 0 | 0.9153 | 0 | p<0.01 | 1
Electrical | 2 | P_loss_IGBT_mean_W | 32 | 0.9571 | 0 | 0.8952 | 0 | p<0.01 | 2
Electrical | 3 | P_loss_IGBT_swing_W | 32 | 0.779 | 0 | 0.6411 | 0 | p<0.01 | 3
Thermal | 1 | IGBT_burst_Tmean_C | 30 | 0.9924 | 0 | 0.954 | 0 | p<0.01 | 1
Thermal | 2 | IGBT_burst_dT_eq_K | 30 | 0.7717 | 0 | 0.623 | 0 | p<0.01 | 2
Thermal | 3 | IGBT_burst_duration_mean_s | 30 | -0.1337 | 0.4812 | -0.0989 | 0.457 | - | 3

## Proposed_metrics
rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
1 | P_rms_MW | 32 | 0.9751 | 0 | 0.9153 | 0 | p<0.01 | 1
2 | Swing_period60s_median_MW_x_E_MJ | 32 | 0.9249 | 0 | 0.8347 | 0 | p<0.01 | 2
3 | Swing_period60s_max_MW_x_E_MJ | 32 | 0.9179 | 0 | 0.8226 | 0 | p<0.01 | 3
4 | Swing_period60s_mean_MW_x_E_MJ | 32 | 0.9124 | 0 | 0.8065 | 0 | p<0.01 | 4
5 | Swing_period60s_median_MW_x_Prms_MW | 32 | 0.893 | 0 | 0.7863 | 0 | p<0.01 | 5
6 | Swing_period60s_mean_MW_x_Prms_MW | 32 | 0.8823 | 0 | 0.7419 | 0 | p<0.01 | 6.5
7 | Swing_period60s_max_MW_x_Prms_MW | 32 | 0.882 | 0 | 0.7661 | 0 | p<0.01 | 6.5
8 | Swing_period10s_max_MW_x_E_MJ | 32 | 0.8666 | 0 | 0.7137 | 0 | p<0.01 | 8.5
9 | P_max_avg_60s_MW | 32 | 0.8519 | 0 | 0.7097 | 0 | p<0.01 | 9.5
10 | P_max_avg_180s_MW | 32 | 0.8468 | 0 | 0.7258 | 0 | p<0.01 | 9.5
11 | Swing_period10s_max_MW_x_Prms_MW | 32 | 0.8482 | 0 | 0.6895 | 0 | p<0.01 | 10.5
12 | Swing_period1s_max_MW | 32 | 0.8068 | 0 | 0.6815 | 0 | p<0.01 | 13.5
13 | Swing_period5s_max_MW | 32 | 0.8123 | 0 | 0.6694 | 0 | p<0.01 | 14.25
14 | P_mean_MW | 32 | 0.8051 | 0 | 0.6799 | 0 | p<0.01 | 15
15 | Energy_MWh | 32 | 0.8051 | 0 | 0.6799 | 0 | p<0.01 | 15
16 | Power_cycle_dP_max_MW | 32 | 0.8116 | 0 | 0.6613 | 0 | p<0.01 | 16
17 | Max_change_in_60s_MW | 32 | 0.8094 | 0 | 0.6532 | 0 | p<0.01 | 17
18 | Swing_period1s_max_MW_x_Prms_MW | 32 | 0.8021 | 0 | 0.6694 | 0 | p<0.01 | 17.25
19 | Max_change_in_1s_MW | 32 | 0.7988 | 0 | 0.6734 | 0 | p<0.01 | 18
20 | P_max_avg_300s_MW | 32 | 0.8017 | 0 | 0.6653 | 0 | p<0.01 | 18.5
21 | Swing_period1s_max_MW_x_E_MJ | 32 | 0.7966 | 0 | 0.6492 | 0 | p<0.01 | 21.75
22 | Damage_proxy_per_h | 32 | 0.7944 | 0 | 0.6492 | 0 | p<0.01 | 22.25
23 | Swing_period10s_max_MW | 32 | 0.8006 | 0 | 0.6371 | 0 | p<0.01 | 22.75
24 | P_max_MW | 32 | 0.7929 | 0 | 0.6452 | 0 | p<0.01 | 23.5
25 | Swing_p95_p05_MW | 32 | 0.7808 | 0 | 0.6411 | 0 | p<0.01 | 25
26 | P_p999_MW | 32 | 0.7918 | 0 | 0.6371 | 0 | p<0.01 | 25.25
27 | Swing_period5s_max_MW_x_Prms_MW | 32 | 0.7731 | 0 | 0.6169 | 0 | p<0.01 | 27.5
28 | Swing_period5s_max_MW_x_E_MJ | 32 | 0.7768 | 0 | 0.6089 | 0 | p<0.01 | 28.5
29 | Swing_period60s_median_MW | 32 | 0.7698 | 0 | 0.6129 | 0 | p<0.01 | 28.75
30 | Swing_period60s_max_MW | 32 | 0.7665 | 0 | 0.6129 | 0 | p<0.01 | 29.25
31 | Swing_filtered_tau0.26s_MW | 32 | 0.7632 | 0 | 0.6048 | 0 | p<0.01 | 31
32 | Swing_avg_1s_MW | 32 | 0.7573 | 0 | 0.5927 | 0 | p<0.01 | 33
33 | P_high_level_MW | 32 | 0.7405 | 0 | 0.6008 | 0 | p<0.01 | 33
34 | Swing_period60s_mean_MW | 32 | 0.7522 | 0 | 0.5927 | 0 | p<0.01 | 33.5
35 | Swing_period10s_mean_MW_x_E_MJ | 32 | 0.7111 | 0 | 0.5927 | 0 | p<0.01 | 36
36 | Step_height_pct_rating | 32 | 0.7185 | 0 | 0.5766 | 0 | p<0.01 | 37
37 | Step_height_MW | 32 | 0.7185 | 0 | 0.5766 | 0 | p<0.01 | 37
38 | Power_cycles_ge_50pct_per_h | 32 | 0.7329 | 0 | 0.5742 | 0 | p<0.01 | 37
39 | Swing_period10s_median_MW_x_E_MJ | 32 | 0.6716 | 0 | 0.5847 | 0 | p<0.01 | 38.5
40 | Swing_period10s_mean_MW_x_Prms_MW | 32 | 0.6888 | 0 | 0.5645 | 0 | p<0.01 | 40
41 | P_low_level_MW | 32 | 0.6965 | 0 | 0.504 | 0 | p<0.01 | 41
42 | Ramp_p99_MW_per_s | 32 | 0.6686 | 0 | 0.504 | 0 | p<0.01 | 42.5
43 | Swing_period10s_median_MW_x_Prms_MW | 32 | 0.6411 | 0.0001 | 0.5363 | 0 | p<0.01 | 43
44 | Swing_period5s_mean_MW_x_E_MJ | 32 | 0.6642 | 0 | 0.504 | 0 | p<0.01 | 43
45 | Swing_period5s_mean_MW_x_Prms_MW | 32 | 0.6433 | 0.0001 | 0.4839 | 0.0001 | p<0.01 | 44.75
46 | Swing_period10s_mean_MW | 32 | 0.6162 | 0.0002 | 0.4758 | 0.0001 | p<0.01 | 46.5
47 | Swing_period5s_median_MW_x_E_MJ | 32 | 0.5568 | 0.0009 | 0.4839 | 0.0001 | p<0.01 | 48.25
48 | Swing_period10s_median_MW | 32 | 0.5898 | 0.0004 | 0.4718 | 0.0001 | p<0.01 | 48.5
49 | Swing_period1s_mean_MW_x_Prms_MW | 32 | 0.6004 | 0.0003 | 0.4395 | 0.0003 | p<0.01 | 49
50 | Swing_period1s_mean_MW_x_E_MJ | 32 | 0.6004 | 0.0003 | 0.4395 | 0.0003 | p<0.01 | 49
51 | Swing_period5s_median_MW_x_Prms_MW | 32 | 0.5466 | 0.0012 | 0.4597 | 0.0001 | p<0.01 | 50.5
52 | P_min_MW | 32 | 0.5817 | 0.0005 | 0.371 | 0.0025 | p<0.01 | 52
53 | Swing_period5s_mean_MW | 32 | 0.5458 | 0.0012 | 0.3911 | 0.0014 | p<0.01 | 52.75
54 | Swing_period5s_median_MW | 32 | 0.4956 | 0.0039 | 0.3911 | 0.0014 | p<0.01 | 53.75
55 | Swing_filtered_tau3.31s_MW | 32 | 0.4978 | 0.0037 | 0.3427 | 0.0055 | p<0.01 | 55.5
56 | Swing_period1s_mean_MW | 32 | 0.4938 | 0.0041 | 0.3508 | 0.0044 | p<0.01 | 55.5
57 | Swing_period1s_median_MW_x_E_MJ | 32 | 0.4751 | 0.006 | 0.3427 | 0.0055 | p<0.01 | 57
58 | Swing_period1s_median_MW_x_Prms_MW | 32 | 0.4703 | 0.0066 | 0.3427 | 0.0055 | p<0.01 | 57.5
59 | Swing_filtered_tau159s_MW | 32 | 0.4337 | 0.0132 | 0.3105 | 0.0123 | p<0.05 | 59
60 | Swing_period1s_median_MW | 32 | 0.335 | 0.0609 | 0.2419 | 0.0531 | - | 60
61 | Power_cycles_ge_10pct_per_h | 32 | 0.326 | 0.0686 | 0.2141 | 0.0882 | - | 61
62 | Power_cycles_ge_30pct_per_h | 32 | 0.3209 | 0.0734 | 0.2118 | 0.0937 | - | 62
63 | Burst_period_CV | 32 | 0.2548 | 0.1594 | 0.1845 | 0.1436 | - | 63
64 | Bursts_per_h | 32 | 0.2168 | 0.2334 | 0.1482 | 0.2416 | - | 65
65 | Transitions_per_h | 32 | 0.2168 | 0.2334 | 0.1482 | 0.2416 | - | 65
66 | Burst_period_mean_s | 32 | -0.2166 | 0.2338 | -0.1517 | 0.2292 | - | 65
67 | Dwell_low_p95_s | 32 | -0.2096 | 0.2497 | -0.1405 | 0.2683 | - | 67
68 | Dwell_low_mean_s | 32 | -0.1946 | 0.2859 | -0.1353 | 0.2835 | - | 68
69 | Dominant_period_s | 32 | -0.187 | 0.3055 | -0.1317 | 0.2979 | - | 69
70 | Dwell_high_p95_s | 32 | 0.1138 | 0.5351 | 0.0697 | 0.5806 | - | 70
71 | Dwell_high_mean_s | 32 | 0.1116 | 0.5431 | 0.0615 | 0.6259 | - | 71
72 | Time_at_high_load_pct | 32 | 0.0815 | 0.6575 | 0.0205 | 0.8709 | - | 72
73 | Peak_to_mean | 32 | -0.0326 | 0.8592 | 0.0142 | 0.9095 | - | 73

## Grid_operator_metrics
rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
1 | Max_change_in_5s_MW | 32 | 0.8079 | 0 | 0.6452 | 0 | p<0.01 | 1
2 | SoCo_band_0.1_0.5Hz_amp_60s_MW | 32 | 0.6298 | 0.0001 | 0.4839 | 0.0001 | p<0.01 | 2
3 | SoCo_band_0.5_0.8Hz_amp_60s_MW | 32 | 0.5499 | 0.0011 | 0.379 | 0.002 | p<0.01 | 3
4 | Swing_avg_4s_MW | 32 | 0.5422 | 0.0013 | 0.3347 | 0.0067 | p<0.01 | 4
5 | Swing_avg_300s_MW | 32 | 0.4238 | 0.0157 | 0.3306 | 0.0075 | p<0.05 | 5
6 | Swing_avg_60s_MW | 32 | 0.4128 | 0.0189 | 0.3105 | 0.0123 | p<0.05 | 6
7 | Ramp_max_MW_per_min | 32 | 0.4054 | 0.0213 | 0.3024 | 0.0148 | p<0.05 | 7
8 | Max_change_in_0.1s_MW | 32 | 0.3739 | 0.035 | 0.2702 | 0.0302 | p<0.05 | 8
9 | SoCo_band_0.8_2Hz_amp_60s_MW | 32 | 0.3361 | 0.06 | 0.2419 | 0.0531 | - | 9
10 | LIPA_band_5_23.75Hz_amp_10s_MW | 32 | 0.3185 | 0.0756 | 0.2258 | 0.0716 | - | 10
11 | ERCOT_changes_gt25pct_in_5s_per_h | 32 | 0.2143 | 0.2388 | 0.159 | 0.21 | - | 11

## Electrical_characteristics
rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
1 | I_IGBT_rms_A | 32 | 0.9751 | 0 | 0.9153 | 0 | p<0.01 | 1
2 | P_loss_IGBT_mean_W | 32 | 0.9571 | 0 | 0.8952 | 0 | p<0.01 | 2
3 | P_loss_IGBT_swing_W | 32 | 0.779 | 0 | 0.6411 | 0 | p<0.01 | 3

## Thermal_characteristics
rank | characteristic | n | spearman_rho | p_spearman | kendall_tau | p_kendall | significant | consensus_rank
1 | IGBT_burst_Tmean_C | 30 | 0.9924 | 0 | 0.954 | 0 | p<0.01 | 1
2 | IGBT_burst_dT_eq_K | 30 | 0.7717 | 0 | 0.623 | 0 | p<0.01 | 2
3 | IGBT_burst_duration_mean_s | 30 | -0.1337 | 0.4812 | -0.0989 | 0.457 | - | 3