## All_results
scenario | chip | duration_s | P_mean_MW | P_max_MW | P_min_MW | Energy_MWh | Peak_to_mean | Swing_p95_p05_MW | Time_at_high_load_pct | Dominant_period_s | Transitions_per_h | Ramp_p99_MW_per_s | P_high_level_MW | P_low_level_MW | Step_height_MW | Step_height_pct_rating | P_p999_MW | Dwell_high_mean_s | Dwell_high_p95_s | Dwell_low_mean_s | Dwell_low_p95_s | Bursts_per_h | Burst_period_mean_s | Burst_period_CV | Power_cycles_ge_10pct_per_h | Power_cycles_ge_30pct_per_h | Power_cycles_ge_50pct_per_h | Power_cycle_dP_max_MW | Damage_proxy_per_h | Swing_filtered_tau0.26s_MW | Swing_filtered_tau3.31s_MW | Swing_filtered_tau159s_MW | Max_change_in_0.1s_MW | Max_change_in_1s_MW | Max_change_in_5s_MW | Max_change_in_60s_MW | Swing_avg_1s_MW | Swing_avg_60s_MW | Swing_avg_900s_MW | Var_share_0_0.017Hz_pct | Var_share_0.017_0.1Hz_pct | Var_share_0.1_0.5Hz_pct | Var_share_0.5_0.8Hz_pct | Var_share_0.8_2Hz_pct | Var_share_2_25Hz_pct | Seam_jump_max_MW | Startup_60s_mean_minus_block_mean_MW | P_rms_MW | P_max_avg_60s_MW | P_max_avg_180s_MW | P_max_avg_300s_MW | Swing_period1s_max_MW | Swing_period1s_max_MW_x_E_MJ | Swing_period1s_max_MW_x_Prms_MW | Swing_period1s_mean_MW | Swing_period1s_mean_MW_x_E_MJ | Swing_period1s_mean_MW_x_Prms_MW | Swing_period1s_median_MW | Swing_period1s_median_MW_x_E_MJ | Swing_period1s_median_MW_x_Prms_MW | Swing_period5s_max_MW | Swing_period5s_max_MW_x_E_MJ | Swing_period5s_max_MW_x_Prms_MW | Swing_period5s_mean_MW | Swing_period5s_mean_MW_x_E_MJ | Swing_period5s_mean_MW_x_Prms_MW | Swing_period5s_median_MW | Swing_period5s_median_MW_x_E_MJ | Swing_period5s_median_MW_x_Prms_MW | Swing_period10s_max_MW | Swing_period10s_max_MW_x_E_MJ | Swing_period10s_max_MW_x_Prms_MW | Swing_period10s_mean_MW | Swing_period10s_mean_MW_x_E_MJ | Swing_period10s_mean_MW_x_Prms_MW | Swing_period10s_median_MW | Swing_period10s_median_MW_x_E_MJ | Swing_period10s_median_MW_x_Prms_MW | Swing_period60s_max_MW | Swing_period60s_max_MW_x_E_MJ | Swing_period60s_max_MW_x_Prms_MW | Swing_period60s_mean_MW | Swing_period60s_mean_MW_x_E_MJ | Swing_period60s_mean_MW_x_Prms_MW | Swing_period60s_median_MW | Swing_period60s_median_MW_x_E_MJ | Swing_period60s_median_MW_x_Prms_MW | ERCOT_changes_gt25pct_in_5s_per_h | LIPA_band_5_23.75Hz_amp_10s_MW | Ramp_max_MW_per_min | Swing_avg_4s_MW | Swing_avg_300s_MW | SoCo_band_0.1_0.5Hz_amp_60s_MW | SoCo_band_0.5_0.8Hz_amp_60s_MW | SoCo_band_0.8_2Hz_amp_60s_MW | I_IGBT_rms_A | I_IGBT_peak_A | I_Diode_rms_A | I_Diode_peak_A | P_loss_IGBT_mean_W | P_loss_IGBT_max_W | P_loss_IGBT_swing_W | P_loss_Diode_mean_W | P_loss_Diode_max_W | P_loss_Diode_swing_W | Switching_share_pct | Diode_share_pct | Loss_ratio_pct | Tj_IGBT_mean_C | Tj_IGBT_max_C | Tj_IGBT_min_C | Tj_IGBT_swing_K | Tj_Diode_mean_C | Tj_Diode_max_C | Tj_Diode_min_C | Tj_Diode_swing_K | T_case_mean_C | T_case_swing_K | IGBT_cycles_per_h | IGBT_dT_max_K | IGBT_dT_mean_K | IGBT_dT_p95_K | IGBT_cycles_dT_lt5_per_h | IGBT_cycles_dT_5_10_per_h | IGBT_cycles_dT_10_20_per_h | IGBT_cycles_dT_ge20_per_h | IGBT_cycle_Tmean_C | IGBT_cycle_duration_mean_s | IGBT_cycle_duration_p95_s | IGBT_grid_cycles_per_h | IGBT_grid_cycle_dT_mean_K | IGBT_grid_cycle_dT_max_K | IGBT_load_cycles_per_h | IGBT_load_cycle_dT_mean_K | IGBT_load_cycle_dT_max_K | IGBT_load_cycle_Tmean_C | IGBT_load_cycle_duration_mean_s | IGBT_burst_cycles_per_h | IGBT_burst_dT_mean_K | IGBT_burst_dT_median_K | IGBT_burst_dT_p95_K | IGBT_burst_dT_max_K | IGBT_burst_dT_eq_K | IGBT_burst_Tmean_C | IGBT_burst_duration_mean_s | Diode_cycles_per_h | Diode_dT_max_K | Diode_dT_mean_K | Diode_dT_p95_K | Diode_cycles_dT_lt5_per_h | Diode_cycles_dT_5_10_per_h | Diode_cycles_dT_10_20_per_h | Diode_cycles_dT_ge20_per_h | Diode_cycle_Tmean_C | Diode_cycle_duration_mean_s | Diode_cycle_duration_p95_s | Diode_grid_cycles_per_h | Diode_grid_cycle_dT_mean_K | Diode_grid_cycle_dT_max_K | Diode_load_cycles_per_h | Diode_load_cycle_dT_mean_K | Diode_load_cycle_dT_max_K | Diode_load_cycle_Tmean_C | Diode_load_cycle_duration_mean_s | Diode_burst_cycles_per_h | Diode_burst_dT_mean_K | Diode_burst_dT_median_K | Diode_burst_dT_p95_K | Diode_burst_dT_max_K | Diode_burst_dT_eq_K | Diode_burst_Tmean_C | Diode_burst_duration_mean_s | Mission_duration_s | IGBT_Nf_eq | IGBT_Nf_eq_dT_ge10 | IGBT_Nf_eq_dT_lt10 | IGBT_Nf_eq_load_cycles | IGBT_Nf_eq_grid_cycles | IGBT_Nf_worst_cycle | IGBT_worst_cycle_dT_K | IGBT_worst_cycle_Tmean_C | Diode_Nf_eq | Diode_Nf_eq_dT_ge10 | Diode_Nf_eq_dT_lt10 | Diode_Nf_eq_load_cycles | Diode_Nf_eq_grid_cycles | Diode_Nf_worst_cycle | Diode_worst_cycle_dT_K | Diode_worst_cycle_Tmean_C | Limiting_device | IGBT_lifetime_years_actual | Diode_lifetime_years_actual
Image_H100_BatchSize_128 | H_100 | 3600 | 0.8033 | 1.5502 | 0.45403 | 0.8033 | 1.9298 | 1.0506 | 33.7089 | 16.0714 | 464 | 2.0633 | 1.4693 | 0.45833 | 1.011 | 50.5479 | 1.5444 | 5.208 | 5.52 | 10.2948 | 11.213 | 231 | 15.5036 | 0.14852 | 236.5 | 228 | 224 | 1.091 | 0.0024742 | 1.0478 | 0.72913 | 0.026758 | 0.30343 | 1.0322 | 1.0942 | 1.0943 | 1.0462 | 0.070776 | 0 | 0.14094 | 76.0438 | 23.3736 | 0.37502 | 0.053716 | 0.012963 | 0.3003 | 0.014918 | 0.92258 | 0.87543 | 0.837 | 0.81596 | 0.91442 | 0.94195 | 0.97698 | 0.12199 | 0.11995 | 0.1229 | 0.0095594 | 0.010055 | 0.010056 | 1.0767 | 7.0481 | 1.4694 | 0.5724 | 2.7618 | 0.59487 | 0.70023 | 2.8426 | 0.63149 | 1.0905 | 10.8153 | 1.2 | 0.91971 | 7.7772 | 0.87336 | 1.0336 | 8.7007 | 0.99532 | 1.0792 | 52.7207 | 1.006 | 1.0475 | 50.4945 | 0.9662 | 1.0454 | 51.1449 | 0.97369 | 440 | 0.23034 | 0.067919 | 0.99221 | 0.0022511 | 0.99818 | 0.18473 | 0.14759 | 424.7443 | 1513.8516 | 125.9241 | 351.4973 | 348.3889 | 699.934 | 490.0576 | 28.9513 | 57.4155 | 39.7901 | 48.7796 | 7.6725 | 0.046973 | 106.7189 | 141.0667 | 40 | 78.5131 | 101.7192 | 130.6145 | 40 | 76.0659 | 100.6432 | 75.9738 | 180000.5 | 101.0667 | 0.7472 | 1.4562 | 179768 | 232 | 0 | 0.5 | 106.7385 | 0.031755 | 0.013 | 179049 | 0.73468 | 1.5034 | 951.5 | 3.1041 | 101.0667 | 105.8221 | 4.1802 | 232 | 9.0547 | 9.1082 | 9.5336 | 9.661 | 9.1554 | 108.6635 | 8.414 | 180000 | 90.6145 | 0.16089 | 0.30872 | 179999.5 | 0 | 0 | 0.5 | 101.7203 | 0.030924 | 0.012 | 179197.5 | 0.15882 | 0.31856 | 802.5 | 0.62377 | 90.6145 | 106.6731 | 4.6047 | 0 | [7 empty] | 3600 | 67553.1837 | inf | 67553.1837 | 67553.1837 | 4.9142e+24 | 33776.5998 | 101.0667 | 90.5333 | 61146.4457 | inf | 61146.4457 | 61146.4457 | 2.5741e+35 | 30573.2228 | 90.6145 | 85.3072 | Diode | 7.7116 | 6.9802
Image_H100_BatchSize_256 | H_100 | 3600 | 0.8033 | 1.215 | 0.47097 | 0.8033 | 1.5125 | 0.72885 | 45.1533 | 18 | 399 | 1.3796 | 1.1947 | 0.4786 | 0.71615 | 35.8074 | 1.2121 | 8.1003 | 8.38 | 9.9176 | 10.52 | 199 | 18.0179 | 0.10673 | 199.5 | 199.5 | 0 | 0.74075 | 3.3897e-06 | 0.72782 | 0.59262 | 0.023894 | 0.71897 | 0.72337 | 0.73686 | 0.7421 | 0.72735 | 0.071874 | 0 | 0.12143 | 86.4639 | 12.9889 | 0.36003 | 0.042305 | 0.023434 | 0.71761 | -0.02658 | 0.87233 | 0.85432 | 0.81402 | 0.81916 | 0.60947 | 0.53264 | 0.54231 | 0.074024 | 0.063323 | 0.064246 | 0.0092519 | 0.0097972 | 0.0097979 | 0.73273 | 3.9051 | 0.80065 | 0.35149 | 1.4693 | 0.3085 | 0.34688 | 1.2743 | 0.26459 | 0.73369 | 7.6411 | 0.78981 | 0.6823 | 5.5871 | 0.59503 | 0.72248 | 5.7901 | 0.6286 | 0.73274 | 37.2011 | 0.66871 | 0.7284 | 35.1088 | 0.63521 | 0.72897 | 34.7271 | 0.62886 | 391 | 0.53561 | 0.069558 | 0.72236 | 0.012842 | 0.86458 | 0.21262 | 0.38585 | 401.6096 | 1186.5471 | 119.0653 | 275.5013 | 345.1124 | 533.8104 | 332.4756 | 28.7679 | 44.1738 | 27.1847 | 49.231 | 7.6944 | 0.046543 | 106.1188 | 137.2976 | 40 | 76.8025 | 101.1695 | 129.3 | 40 | 75.4578 | 100.1002 | 75.1216 | 180000.5 | 97.2976 | 0.73951 | 1.1333 | 179801 | 199 | 0 | 0.5 | 106.1379 | 0.030906 | 0.013 | 177330.5 | 0.72869 | 1.1554 | 2670 | 1.458 | 97.2976 | 109.6373 | 1.3978 | 199 | 6.3557 | 6.3888 | 6.5353 | 6.5932 | 6.3773 | 106.5213 | 7.4983 | 180003 | 89.3 | 0.15982 | 0.24245 | 180002.5 | 0 | 0 | 0.5 | 101.1707 | 0.029139 | 0.012 | 179000.5 | 0.15853 | 0.2458 | 1002.5 | 0.39176 | 89.3 | 109.6444 | 3.2941 | 0 | [7 empty] | 3600 | 83161.7975 | inf | 83161.7975 | 83161.7975 | 2.1383e+26 | 41580.8988 | 97.2976 | 88.6488 | 66149.9871 | inf | 66149.9871 | 66149.9871 | 6.3578e+36 | 33074.9936 | 89.3 | 84.65 | Diode | 9.4934 | 7.5514
Image_H100_BatchSize_512 | H_100 | 3600 | 0.8033 | 2 | 0.44914 | 0.8033 | 2.4897 | 1.5114 | 16.4356 | 14.0625 | 312 | 2.7442 | 1.957 | 0.45874 | 1.4983 | 74.9132 | 1.9953 | 3.32 | 3.34 | 17.5289 | 11 | 156 | 20.849 | 2.3419 | 243.5 | 239.5 | 156 | 1.536 | 1.2387 | 1.5038 | 0.78566 | 0.05031 | 1.1307 | 1.4284 | 1.5448 | 1.5501 | 1.5043 | 0.13957 | 0 | 0.24609 | 64.7699 | 34.2835 | 0.57758 | 0.078517 | 0.044399 | 0.74057 | -0.041514 | 0.94937 | 0.88623 | 0.83791 | 0.83372 | 1.3213 | 1.7435 | 1.8199 | 0.15689 | 0.17984 | 0.18535 | 0.03074 | 0.020103 | 0.02011 | 1.5339 | 11.1031 | 2.396 | 0.67256 | 3.4644 | 0.77473 | 0.64419 | 2.128 | 0.45074 | 1.5349 | 14.8428 | 1.7807 | 1.0807 | 9.1657 | 1.0756 | 1.0587 | 7.4928 | 0.78094 | 1.5297 | 79.6149 | 1.6263 | 1.2143 | 59.1898 | 1.18 | 1.5175 | 72.6247 | 1.4934 | 317 | 0.84326 | 0.13957 | 1.1025 | 0.050727 | 1.3685 | 0.32576 | 0.60436 | 437.0793 | 1953.1287 | 129.581 | 453.4919 | 350.2109 | 935.7165 | 730.1719 | 29.0533 | 75.9053 | 58.6516 | 48.5321 | 7.6604 | 0.047213 | 106.8414 | 146.2724 | 40 | 78.5267 | 101.8134 | 132.3367 | 40 | 77.5162 | 100.7341 | 77.2239 | 180000.5 | 106.2724 | 0.7515 | 1.972 | 179760.5 | 84 | 155.5 | 0.5 | 106.8613 | 0.032313 | 0.013 | 177895.5 | 0.73028 | 2.0269 | 2105 | 2.5443 | 106.2724 | 109.6765 | 1.9719 | 239.5 | 11.0787 | 13.42 | 13.7455 | 13.8351 | 13.1681 | 110.0387 | 7.8725 | 180000 | 92.3367 | 0.16149 | 0.41331 | 179999.5 | 0 | 0 | 0.5 | 101.8146 | 0.031779 | 0.012 | 178035 | 0.15811 | 0.42564 | 1965 | 0.46707 | 92.3367 | 104.787 | 1.9638 | 0 | [7 empty] | 3600 | 51210.2427 | inf | 51210.2427 | 51210.2427 | 5.1855e+22 | 25606.6413 | 106.2724 | 93.1362 | 55238.6259 | inf | 55238.6259 | 55238.6259 | 5.0771e+33 | 27619.3129 | 92.3367 | 86.1684 | IGBT | 5.8459 | 6.3058
Image_H100_ImageSize_16 | H_100 | 3600 | 0.8033 | 1.3142 | 0.56126 | 0.8033 | 1.636 | 0.72392 | 32.7044 | 12 | 599 | 1.3695 | 1.2729 | 0.5728 | 0.70012 | 35.0061 | 1.3077 | 3.9323 | 4.16 | 8.0807 | 8.68 | 299 | 12.013 | 0.040278 | 303.5 | 292 | 0 | 0.74665 | 4.3387e-06 | 0.72045 | 0.41438 | 0.014743 | 0.65282 | 0.70996 | 0.74229 | 0.74469 | 0.7183 | 0.020573 | 0 | 0.12879 | 76.108 | 22.97 | 0.67663 | 0.093389 | 0.023176 | 0.59326 | -0.0030773 | 0.85991 | 0.81309 | 0.80765 | 0.80715 | 0.63301 | 0.60936 | 0.62275 | 0.10935 | 0.10247 | 0.10398 | 0.0066616 | 0.0046484 | 0.0046485 | 0.73419 | 4.0901 | 0.83842 | 0.49919 | 2.2329 | 0.46738 | 0.69876 | 2.8135 | 0.59701 | 0.7353 | 6.2814 | 0.67213 | 0.71599 | 5.753 | 0.61426 | 0.71796 | 5.9985 | 0.64072 | 0.73043 | 35.2601 | 0.62909 | 0.72275 | 34.835 | 0.62149 | 0.72302 | 34.8648 | 0.62167 | 304 | 0.43691 | 0.015417 | 0.61505 | 0.0062398 | 0.60965 | 0.26273 | 0.39163 | 395.896 | 1283.4068 | 117.3714 | 297.9909 | 344.3315 | 582.1214 | 335.0751 | 28.7242 | 48.0448 | 27.2722 | 49.3398 | 7.6997 | 0.04644 | 105.9667 | 138.0255 | 40 | 76.1665 | 101.0294 | 129.3379 | 40 | 75.4709 | 99.9616 | 75.3354 | 180000.5 | 98.0255 | 0.73768 | 1.2261 | 179702 | 298 | 0 | 0.5 | 105.9857 | 0.031458 | 0.013 | 178516 | 0.72752 | 1.2512 | 1484.5 | 1.9589 | 98.0255 | 108.3042 | 2.6053 | 298 | 6.3702 | 6.3961 | 6.5838 | 6.6776 | 6.4024 | 107.4997 | 5.81 | 180000 | 89.3379 | 0.15957 | 0.26185 | 179999.5 | 0 | 0 | 0.5 | 101.0305 | 0.029364 | 0.012 | 178978.5 | 0.15777 | 0.26614 | 1021.5 | 0.47595 | 89.3379 | 110.3477 | 3.2779 | 0 | [7 empty] | 3600 | 79848.5959 | inf | 79848.5959 | 79848.5959 | 9.6402e+25 | 39924.298 | 98.0255 | 89.0127 | 65999.4392 | inf | 65999.4392 | 65999.4392 | 3.4394e+36 | 32999.7196 | 89.3379 | 84.669 | Diode | 9.1151 | 7.5342
Image_H100_ImageSize_32 | H_100 | 3600 | 0.8033 | 1.5502 | 0.45403 | 0.8033 | 1.9298 | 1.0506 | 33.7089 | 16.0714 | 464 | 2.0633 | 1.4693 | 0.45833 | 1.011 | 50.5479 | 1.5444 | 5.208 | 5.52 | 10.2948 | 11.213 | 231 | 15.5036 | 0.14852 | 236.5 | 228 | 224 | 1.091 | 0.0024742 | 1.0478 | 0.72913 | 0.026758 | 0.30343 | 1.0322 | 1.0942 | 1.0943 | 1.0462 | 0.070776 | 0 | 0.14094 | 76.0438 | 23.3736 | 0.37502 | 0.053716 | 0.012963 | 0.3003 | 0.014918 | 0.92258 | 0.87543 | 0.837 | 0.81596 | 0.91442 | 0.94195 | 0.97698 | 0.12199 | 0.11995 | 0.1229 | 0.0095594 | 0.010055 | 0.010056 | 1.0767 | 7.0481 | 1.4694 | 0.5724 | 2.7618 | 0.59487 | 0.70023 | 2.8426 | 0.63149 | 1.0905 | 10.8153 | 1.2 | 0.91971 | 7.7772 | 0.87336 | 1.0336 | 8.7007 | 0.99532 | 1.0792 | 52.7207 | 1.006 | 1.0475 | 50.4945 | 0.9662 | 1.0454 | 51.1449 | 0.97369 | 440 | 0.23034 | 0.067919 | 0.99221 | 0.0022511 | 0.99818 | 0.18473 | 0.14759 | 424.7443 | 1513.8516 | 125.9241 | 351.4973 | 348.3889 | 699.934 | 490.0576 | 28.9513 | 57.4155 | 39.7901 | 48.7796 | 7.6725 | 0.046973 | 106.7189 | 141.0667 | 40 | 78.5131 | 101.7192 | 130.6145 | 40 | 76.0659 | 100.6432 | 75.9738 | 180000.5 | 101.0667 | 0.7472 | 1.4562 | 179768 | 232 | 0 | 0.5 | 106.7385 | 0.031755 | 0.013 | 179049 | 0.73468 | 1.5034 | 951.5 | 3.1041 | 101.0667 | 105.8221 | 4.1802 | 232 | 9.0547 | 9.1082 | 9.5336 | 9.661 | 9.1554 | 108.6635 | 8.414 | 180000 | 90.6145 | 0.16089 | 0.30872 | 179999.5 | 0 | 0 | 0.5 | 101.7203 | 0.030924 | 0.012 | 179197.5 | 0.15882 | 0.31856 | 802.5 | 0.62377 | 90.6145 | 106.6731 | 4.6047 | 0 | [7 empty] | 3600 | 67553.1837 | inf | 67553.1837 | 67553.1837 | 4.9142e+24 | 33776.5998 | 101.0667 | 90.5333 | 61146.4457 | inf | 61146.4457 | 61146.4457 | 2.5741e+35 | 30573.2228 | 90.6145 | 85.3072 | Diode | 7.7116 | 6.9802
Image_H100_ImageSize_64 | H_100 | 3600 | 0.8033 | 1.1303 | 0.24342 | 0.8033 | 1.407 | 0.87041 | 64.3933 | 21.9512 | 351 | 1.5682 | 1.1031 | 0.25235 | 0.85077 | 42.5386 | 1.1275 | 13.2267 | 14.14 | 7.3102 | 8.24 | 175 | 20.5369 | 0.18647 | 179.5 | 175.5 | 0 | 0.88011 | 5.9861e-05 | 0.8687 | 0.71098 | 0.026278 | 0.83326 | 0.83858 | 0.87673 | 0.88215 | 0.86832 | 0.0895 | 0 | 0.1568 | 89.7647 | 9.6777 | 0.31453 | 0.054986 | 0.031336 | 0.83311 | 0.040884 | 0.89208 | 0.86315 | 0.81949 | 0.82028 | 0.75095 | 0.55262 | 0.57925 | 0.082163 | 0.059085 | 0.060779 | 0.014711 | 0.015583 | 0.015583 | 0.87079 | 4.2152 | 0.87422 | 0.37603 | 1.2924 | 0.28478 | 0.15284 | 0.47831 | 0.1014 | 0.87353 | 8.7052 | 0.89236 | 0.66091 | 4.7288 | 0.53074 | 0.85572 | 5.0579 | 0.61348 | 0.87177 | 43.9909 | 0.80225 | 0.86589 | 41.7346 | 0.77221 | 0.86513 | 41.3086 | 0.76925 | 329 | 0.6215 | 0.0895 | 0.86362 | 0.017481 | 1.2162 | 0.22807 | 0.45725 | 410.7055 | 1103.77 | 121.762 | 256.2815 | 346.3788 | 493.0898 | 387.0979 | 28.8388 | 40.8973 | 31.9075 | 49.0555 | 7.6859 | 0.046709 | 106.4258 | 136.902 | 40 | 77.2536 | 101.4568 | 129.564 | 40 | 75.6921 | 100.3848 | 75.7391 | 179997.5 | 96.902 | 0.7425 | 1.0451 | 179822 | 175 | 0 | 0.5 | 106.445 | 0.031078 | 0.013 | 172935 | 0.72419 | 1.0691 | 7062.5 | 1.191 | 96.902 | 108.6131 | 0.55177 | 175 | 7.1455 | 7.2145 | 7.3282 | 7.4802 | 7.1856 | 106.0905 | 5.6921 | 179997 | 89.564 | 0.16024 | 0.22382 | 179996.5 | 0 | 0 | 0.5 | 101.4579 | 0.029482 | 0.012 | 176292.5 | 0.15794 | 0.22786 | 3704.5 | 0.26966 | 89.564 | 115.6292 | 0.89147 | 0 | [7 empty] | 3600 | 85028.795 | inf | 85028.795 | 85028.795 | 7.3448e+26 | 42514.3977 | 96.902 | 88.451 | 65108.1052 | inf | 65108.1052 | 65108.1052 | 1.6507e+37 | 32554.0526 | 89.564 | 84.782 | Diode | 9.7065 | 7.4324
Image_H100_ModelSize_128 | H_100 | 3600 | 0.8033 | 1.5502 | 0.45403 | 0.8033 | 1.9298 | 1.0506 | 33.7089 | 16.0714 | 464 | 2.0633 | 1.4693 | 0.45833 | 1.011 | 50.5479 | 1.5444 | 5.208 | 5.52 | 10.2948 | 11.213 | 231 | 15.5036 | 0.14852 | 236.5 | 228 | 224 | 1.091 | 0.0024742 | 1.0478 | 0.72913 | 0.026758 | 0.30343 | 1.0322 | 1.0942 | 1.0943 | 1.0462 | 0.070776 | 0 | 0.14094 | 76.0438 | 23.3736 | 0.37502 | 0.053716 | 0.012963 | 0.3003 | 0.014918 | 0.92258 | 0.87543 | 0.837 | 0.81596 | 0.91442 | 0.94195 | 0.97698 | 0.12199 | 0.11995 | 0.1229 | 0.0095594 | 0.010055 | 0.010056 | 1.0767 | 7.0481 | 1.4694 | 0.5724 | 2.7618 | 0.59487 | 0.70023 | 2.8426 | 0.63149 | 1.0905 | 10.8153 | 1.2 | 0.91971 | 7.7772 | 0.87336 | 1.0336 | 8.7007 | 0.99532 | 1.0792 | 52.7207 | 1.006 | 1.0475 | 50.4945 | 0.9662 | 1.0454 | 51.1449 | 0.97369 | 440 | 0.23034 | 0.067919 | 0.99221 | 0.0022511 | 0.99818 | 0.18473 | 0.14759 | 424.7443 | 1513.8516 | 125.9241 | 351.4973 | 348.3889 | 699.934 | 490.0576 | 28.9513 | 57.4155 | 39.7901 | 48.7796 | 7.6725 | 0.046973 | 106.7189 | 141.0667 | 40 | 78.5131 | 101.7192 | 130.6145 | 40 | 76.0659 | 100.6432 | 75.9738 | 180000.5 | 101.0667 | 0.7472 | 1.4562 | 179768 | 232 | 0 | 0.5 | 106.7385 | 0.031755 | 0.013 | 179049 | 0.73468 | 1.5034 | 951.5 | 3.1041 | 101.0667 | 105.8221 | 4.1802 | 232 | 9.0547 | 9.1082 | 9.5336 | 9.661 | 9.1554 | 108.6635 | 8.414 | 180000 | 90.6145 | 0.16089 | 0.30872 | 179999.5 | 0 | 0 | 0.5 | 101.7203 | 0.030924 | 0.012 | 179197.5 | 0.15882 | 0.31856 | 802.5 | 0.62377 | 90.6145 | 106.6731 | 4.6047 | 0 | [7 empty] | 3600 | 67553.1837 | inf | 67553.1837 | 67553.1837 | 4.9142e+24 | 33776.5998 | 101.0667 | 90.5333 | 61146.4457 | inf | 61146.4457 | 61146.4457 | 2.5741e+35 | 30573.2228 | 90.6145 | 85.3072 | Diode | 7.7116 | 6.9802
Image_H100_ModelSize_256 | H_100 | 3600 | 0.8033 | 1.6911 | 0.37693 | 0.8033 | 2.1051 | 1.29 | 32.9644 | 28.125 | 255 | 2.3071 | 1.6545 | 0.38255 | 1.272 | 63.5989 | 1.6841 | 9.2846 | 9.56 | 18.8965 | 20.58 | 127 | 28.1811 | 0.044136 | 127.5 | 127.5 | 127.5 | 1.3018 | 0.057515 | 1.2883 | 1.151 | 0.04492 | 1.2868 | 1.2875 | 1.3057 | 1.3126 | 1.2879 | 0.07961 | 0 | 0.066424 | 90.502 | 9.0844 | 0.27694 | 0.047383 | 0.022924 | 1.2831 | -0.024543 | 0.98893 | 0.91294 | 0.84791 | 0.82151 | 1.1209 | 1.2421 | 1.3032 | 0.085755 | 0.089498 | 0.092511 | 0.0015863 | 0.00061013 | 0.00061013 | 1.2948 | 9.2715 | 1.926 | 0.41181 | 2.0655 | 0.45684 | 0.036101 | 0.21493 | 0.042987 | 1.2958 | 19.4712 | 1.9986 | 0.81092 | 8.2571 | 0.92378 | 1.2275 | 8.5584 | 1.0688 | 1.2951 | 66.5582 | 1.3505 | 1.2898 | 62.1688 | 1.275 | 1.2889 | 60.4972 | 1.2472 | 255 | 0.95754 | 0.07961 | 1.2822 | 0.010771 | 1.0031 | 0.39342 | 0.69028 | 455.295 | 1651.4336 | 134.9814 | 383.4421 | 352.9968 | 772.2002 | 605.7876 | 29.2092 | 63.118 | 49.0847 | 48.1586 | 7.6423 | 0.047579 | 107.5488 | 143.6624 | 40 | 81.2155 | 102.4782 | 132.0866 | 40 | 77.1454 | 101.393 | 77.3829 | 179997.5 | 103.6624 | 0.75805 | 1.6365 | 179870 | 0 | 127 | 0.5 | 107.569 | 0.032703 | 0.013 | 178483 | 0.74445 | 1.6956 | 1514.5 | 2.3611 | 103.6624 | 112.6473 | 2.7053 | 127 | 11.4739 | 11.5379 | 11.8003 | 11.878 | 11.5155 | 109.973 | 16.0853 | 180000 | 92.0866 | 0.16239 | 0.34498 | 179999.5 | 0 | 0 | 0.5 | 102.4794 | 0.031588 | 0.012 | 179574.5 | 0.16081 | 0.35229 | 425.5 | 0.82985 | 92.0866 | 105.922 | 8.9894 | 0 | [7 empty] | 3600 | 58757.7116 | inf | 58757.7116 | 58757.7116 | 4.7814e+23 | 29379.0042 | 103.6624 | 91.8312 | 56054.7124 | inf | 56054.7124 | 56054.7124 | 3.3855e+34 | 28027.3562 | 92.0866 | 86.0433 | Diode | 6.7075 | 6.3989
Image_H100_ModelSize_512 | H_100 | 3600 | 0.8033 | 1.9424 | 0.36713 | 0.8033 | 2.418 | 1.5181 | 28.5533 | 81.8182 | 88 | 1.5689 | 1.8708 | 0.37249 | 1.4983 | 74.9168 | 1.9024 | 23.3395 | 25.594 | 58.4218 | 61.84 | 43 | 81.535 | 0.029494 | 48 | 44 | 44 | 1.5265 | 0.35232 | 1.5131 | 1.5034 | 0.14126 | 0.23905 | 1.419 | 1.5231 | 1.575 | 1.5125 | 0.54476 | 0 | 62.8663 | 32.8057 | 4.2261 | 0.080502 | 0.012778 | 0.00858 | 0.016577 | -0.097917 | 1.0441 | 1.0222 | 0.94044 | 0.85185 | 1.2595 | 1.5656 | 1.6494 | 0.044336 | 0.053387 | 0.05502 | 0.00048787 | 0.00018417 | 0.00018417 | 1.5125 | 11.8046 | 2.4399 | 0.18457 | 0.96799 | 0.21964 | 0.0028052 | 0.0053152 | 0.001063 | 1.5149 | 23.4085 | 2.5005 | 0.35662 | 4.1342 | 0.46937 | 0.0077248 | 0.029367 | 0.0029368 | 1.5228 | 87.239 | 1.8179 | 1.4219 | 70.8071 | 1.5037 | 1.5187 | 83.8167 | 1.7697 | 88 | 0.17775 | 0.5391 | 1.5103 | 0.052448 | 1.0782 | 0.19097 | 0.14716 | 480.7117 | 1896.8528 | 142.5167 | 440.4253 | 357.0742 | 904.6894 | 724.2578 | 29.4375 | 73.4906 | 58.3996 | 47.6221 | 7.6162 | 0.048115 | 108.3836 | 147.3183 | 40 | 84.455 | 103.2503 | 133.922 | 40 | 77.1941 | 102.1567 | 76.6875 | 180000.5 | 107.3183 | 0.7676 | 1.8807 | 179956 | 0 | 44 | 0.5 | 108.4046 | 0.03358 | 0.013 | 177867 | 0.75098 | 1.9018 | 2133.5 | 2.1533 | 107.3183 | 115.001 | 2.1062 | 44 | 14.3471 | 14.5905 | 15.2697 | 15.4902 | 14.6088 | 111.3666 | 48.7452 | 180000 | 93.922 | 0.16372 | 0.39419 | 179999.5 | 0 | 0 | 0.5 | 103.2515 | 0.032003 | 0.012 | 179664.5 | 0.16251 | 0.40659 | 335.5 | 0.80848 | 93.922 | 113.0114 | 11.7236 | 0 | [7 empty] | 3600 | 48505.1797 | inf | 48505.1797 | 48505.1797 | 5.4247e+22 | 24254.0559 | 107.3183 | 93.6592 | 50378.978 | inf | 50378.978 | 50378.978 | 4.1214e+33 | 25189.489 | 93.922 | 86.961 | IGBT | 5.5371 | 5.751
Text_H100_BatchSize2 | H_100 | 3600 | 0.8033 | 0.94546 | 0.3642 | 0.8033 | 1.177 | 0.5202 | 88.9067 | 45 | 176 | 0.67003 | 0.85367 | 0.37468 | 0.47899 | 23.9496 | 0.93544 | 36.5216 | 43.42 | 4.2636 | 4.82 | 87 | 40.6368 | 0.30187 | 84 | 0 | 0 | 0.56681 | 5.8488e-09 | 0.50713 | 0.30785 | 0.099195 | 0.073195 | 0.46733 | 0.56431 | 0.57069 | 0.4998 | 0.34725 | 0 | 44.0966 | 33.5729 | 21.1307 | 0.99992 | 0.13405 | 0.065896 | 0.016875 | 0.024779 | 0.81517 | 0.84355 | 0.83315 | 0.83452 | 0.41288 | 0.265 | 0.26972 | 0.050243 | 0.037891 | 0.038036 | 0.032146 | 0.027208 | 0.027209 | 0.5281 | 2.0437 | 0.41835 | 0.1412 | 0.53098 | 0.10802 | 0.073059 | 0.30832 | 0.06168 | 0.52792 | 4.0017 | 0.4086 | 0.19521 | 1.4897 | 0.15154 | 0.084669 | 0.71982 | 0.072012 | 0.50114 | 21.4749 | 0.36187 | 0.32064 | 15.1735 | 0.25604 | 0.26262 | 13.1928 | 0.2212 | 116 | 0.059827 | 0.33177 | 0.33683 | 0.078585 | 0.48375 | 0.14127 | 0.061885 | 375.2941 | 923.3005 | 111.2636 | 214.3787 | 341.6085 | 406.1211 | 229.5998 | 28.5717 | 33.8552 | 18.9716 | 49.7231 | 7.7183 | 0.046082 | 105.6216 | 133.4617 | 40 | 74.263 | 100.726 | 127.5906 | 40 | 74.067 | 99.6635 | 74.0481 | 180000.5 | 93.4617 | 0.73128 | 0.81888 | 179997 | 3 | 0 | 0.5 | 105.6401 | 0.036869 | 0.013 | 176921.5 | 0.72619 | 0.87976 | 3079 | 1.0239 | 93.4617 | 105.6071 | 1.5365 | 3 | 5.4903 | 5.569 | 5.8801 | 5.8801 | 5.6235 | 119.3969 | 55.9797 | 180000 | 87.5906 | 0.15869 | 0.17724 | 179999.5 | 0 | 0 | 0.5 | 100.7271 | 0.030941 | 0.012 | 177154 | 0.15771 | 0.19078 | 2846 | 0.21983 | 87.5906 | 103.5582 | 1.2535 | 0 | [7 empty] | 3600 | 103472.0952 | inf | 103472.0952 | 103472.0952 | 4.3246e+28 | 51736.0476 | 93.4617 | 86.7309 | 73384.8099 | inf | 73384.8099 | 73384.8099 | 6.9034e+38 | 36692.405 | 87.5906 | 83.7953 | Diode | 11.8119 | 8.3773
Text_H100_BatchSize16 | H_100 | 3600 | 0.8033 | 1.018 | 0.18971 | 0.8033 | 1.2673 | 0.77198 | 85.6422 | 13.4328 | 536 | 1.7048 | 0.91924 | 0.20611 | 0.71313 | 35.6564 | 1.0069 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 352 | 268 | 0 | 0.80419 | 1.2171e-05 | 0.7229 | 0.28569 | 0.0092759 | 0.12383 | 0.78922 | 0.82273 | 0.82536 | 0.70356 | 0.037152 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.081189 | 0.009089 | 0.83422 | 0.82427 | 0.81209 | 0.80857 | 0.68357 | 0.44018 | 0.46108 | 0.15539 | 0.10397 | 0.10652 | 0.062593 | 0.052909 | 0.053101 | 0.79943 | 3.3657 | 0.70053 | 0.43584 | 1.5818 | 0.33461 | 0.34234 | 1.49 | 0.30116 | 0.80769 | 6.6649 | 0.68652 | 0.66948 | 5.2965 | 0.55209 | 0.76206 | 5.8457 | 0.61561 | 0.78168 | 38.131 | 0.65897 | 0.7705 | 37.1378 | 0.64273 | 0.77098 | 37.3601 | 0.64354 | 268 | 0.065105 | 0.037152 | 0.39111 | 0.006674 | 0.80098 | 0.21051 | 0.11513 | 384.0682 | 994.1323 | 113.8648 | 230.825 | 342.7504 | 439.9593 | 337.7796 | 28.6357 | 36.6025 | 27.9889 | 49.5616 | 7.7105 | 0.046232 | 105.6901 | 134.7301 | 40 | 75.413 | 100.7771 | 128.3306 | 40 | 74.9528 | 99.7125 | 74.7465 | 180000.5 | 94.7301 | 0.73397 | 0.89112 | 179732 | 268 | 0 | 0.5 | 105.7088 | 0.037311 | 0.013 | 177095.5 | 0.71924 | 0.93738 | 2905 | 1.6322 | 94.7301 | 106.2588 | 1.6913 | 268 | 6.0736 | 6.0899 | 6.3084 | 6.424 | 6.1022 | 104.255 | 6.1702 | 180000 | 88.3306 | 0.15906 | 0.19251 | 179999.5 | 0 | 0 | 0.5 | 100.7782 | 0.032754 | 0.012 | 177073 | 0.15635 | 0.20234 | 2927 | 0.32309 | 88.3306 | 101.2711 | 1.3756 | 0 | [7 empty] | 3600 | 96181.2709 | inf | 96181.2709 | 96181.2709 | 1.3646e+28 | 48090.6355 | 94.7301 | 87.365 | 70145.6149 | inf | 70145.6149 | 70145.6149 | 2.4998e+38 | 35072.8075 | 88.3306 | 84.1653 | Diode | 10.9796 | 8.0075
Text_H100_BatchSize32 | H_100 | 3600 | 0.8033 | 0.99716 | 0.18458 | 0.8033 | 1.2413 | 0.76581 | 87.36 | 14.2857 | 503 | 1.7563 | 0.90302 | 0.20048 | 0.70254 | 35.1268 | 0.98553 | 12.5153 | 12.84 | 1.7927 | 1.96 | 251 | 14.308 | 0.045065 | 404 | 251.5 | 0 | 0.78744 | 1.018e-05 | 0.70032 | 0.26146 | 0.007016 | 0.50398 | 0.78255 | 0.8111 | 0.81257 | 0.67223 | 0.025405 | 0 | 0.062454 | 35.0869 | 62.2372 | 1.967 | 0.54333 | 0.10309 | 0.42999 | -0.0077049 | 0.83091 | 0.82068 | 0.81048 | 0.80754 | 0.69131 | 0.4214 | 0.44438 | 0.15417 | 0.10447 | 0.10693 | 0.071695 | 0.060898 | 0.060918 | 0.78995 | 3.1248 | 0.64686 | 0.42335 | 1.5595 | 0.32864 | 0.30314 | 1.3169 | 0.26501 | 0.78138 | 6.4466 | 0.66303 | 0.63134 | 4.9742 | 0.51712 | 0.75389 | 5.7205 | 0.59988 | 0.77112 | 37.6462 | 0.64786 | 0.76184 | 36.7188 | 0.63301 | 0.76186 | 36.6418 | 0.63218 | 252 | 0.31817 | 0.01923 | 0.34266 | 0.0012444 | 0.87443 | 0.17972 | 0.23839 | 382.5423 | 973.7871 | 113.4124 | 226.1011 | 342.5499 | 430.2008 | 334.5476 | 28.6244 | 35.8112 | 27.7354 | 49.5899 | 7.7119 | 0.046206 | 105.6397 | 134.7673 | 40 | 75.4523 | 100.7297 | 128.3307 | 40 | 74.9516 | 99.6656 | 74.8182 | 180000.5 | 94.7673 | 0.7335 | 0.8773 | 179749 | 251 | 0 | 0.5 | 105.6584 | 0.038761 | 0.013 | 177511 | 0.71958 | 0.91453 | 2489.5 | 1.7265 | 94.7673 | 106.3771 | 2.0555 | 251 | 6.0218 | 6.0361 | 6.2429 | 6.3184 | 6.0427 | 104.2889 | 6.6494 | 180000 | 88.3307 | 0.159 | 0.18959 | 179999.5 | 0 | 0 | 0.5 | 100.7309 | 0.032169 | 0.012 | 177596.5 | 0.15642 | 0.19771 | 2403.5 | 0.34907 | 88.3307 | 101.0866 | 1.6329 | 0 | [7 empty] | 3600 | 95975.9992 | inf | 95975.9992 | 95975.9992 | 1.6822e+28 | 47987.9996 | 94.7673 | 87.3837 | 70145.1745 | inf | 70145.1745 | 70145.1745 | 3.0809e+38 | 35072.5873 | 88.3307 | 84.1654 | Diode | 10.9562 | 8.0074
Text_H100_Deepspeedds_z1 | H_100 | 3600 | 0.8033 | 1.1511 | 0.1985 | 0.8033 | 1.433 | 0.92198 | 73.1756 | 13.0435 | 1104 | 2.1884 | 1.0066 | 0.22305 | 0.7836 | 39.1798 | 1.1419 | 4.7976 | 8.81 | 1.7197 | 2.96 | 551 | 6.5102 | 0.43421 | 1248.5 | 276 | 0 | 0.92534 | 0.00022912 | 0.89344 | 0.38189 | 0.021539 | 0.24586 | 0.92514 | 0.94487 | 0.94487 | 0.88629 | 0.0565 | 0 | 0.15517 | 45.5815 | 51.7663 | 1.9907 | 0.44603 | 0.060206 | 0.21442 | -0.0094018 | 0.85978 | 0.83983 | 0.81721 | 0.81782 | 0.83996 | 0.61033 | 0.64511 | 0.3098 | 0.24703 | 0.25254 | 0.28736 | 0.24665 | 0.24853 | 0.92755 | 4.0988 | 0.85765 | 0.68413 | 2.5981 | 0.55785 | 0.74413 | 2.7018 | 0.57651 | 0.92782 | 8.2685 | 0.85956 | 0.86226 | 6.8628 | 0.73575 | 0.92058 | 6.9766 | 0.75765 | 0.9246 | 46.0134 | 0.81283 | 0.92198 | 44.4379 | 0.79262 | 0.92195 | 44.455 | 0.79286 | 268 | 0.15753 | 0.0352 | 0.5321 | 0.013313 | 0.94231 | 0.36689 | 0.14954 | 395.8351 | 1124.1496 | 117.3533 | 261.0134 | 344.3232 | 503.0668 | 409.0953 | 28.7237 | 41.7012 | 33.7455 | 49.341 | 7.6998 | 0.046439 | 106.0335 | 136.2177 | 40 | 75.9689 | 101.0961 | 128.846 | 40 | 75.2037 | 100.0283 | 75.081 | 180000.5 | 96.2177 | 0.73767 | 1.0471 | 179719 | 281 | 0 | 0.5 | 106.0524 | 0.033801 | 0.013 | 178616 | 0.71086 | 1.0607 | 1384.5 | 4.1958 | 96.2177 | 106.5082 | 3.1331 | 281 | 7.2907 | 7.3464 | 7.4517 | 7.4966 | 7.3295 | 105.0855 | 5.0006 | 180000 | 88.846 | 0.15957 | 0.22504 | 179999.5 | 0 | 0 | 0.5 | 101.0972 | 0.03317 | 0.012 | 178612.5 | 0.15471 | 0.22816 | 1387.5 | 0.78575 | 88.846 | 101.0522 | 3.0156 | 0 | [7 empty] | 3600 | 88373.2891 | inf | 88373.2891 | 88373.2891 | 1.3245e+27 | 44186.6448 | 96.2177 | 88.1088 | 67987.6074 | inf | 67987.6074 | 67987.6074 | 3.3382e+37 | 33993.8037 | 88.846 | 84.423 | Diode | 10.0883 | 7.7611
Text_H100_Deepspeedds_z2 | H_100 | 3600 | 0.8033 | 1.0446 | 0.19433 | 0.8033 | 1.3003 | 0.78107 | 84.7 | 13.4328 | 559 | 1.5899 | 0.92662 | 0.21031 | 0.71631 | 35.8156 | 1.0262 | 10.9229 | 11.56 | 1.9639 | 2.14 | 279 | 12.8576 | 0.14207 | 419.5 | 275.5 | 0 | 0.82427 | 1.6049e-05 | 0.73555 | 0.29734 | 0.012159 | 0.73569 | 0.80382 | 0.84405 | 0.84412 | 0.72974 | 0.041142 | 0 | 0.3005 | 45.118 | 51.8542 | 2.128 | 0.42275 | 0.17648 | 0.71233 | -0.0082566 | 0.83616 | 0.82598 | 0.81338 | 0.81083 | 0.72175 | 0.45335 | 0.48291 | 0.16783 | 0.11472 | 0.11747 | 0.073916 | 0.062622 | 0.062735 | 0.81304 | 3.3864 | 0.70308 | 0.45058 | 1.638 | 0.34682 | 0.39787 | 1.7305 | 0.35025 | 0.81561 | 6.8252 | 0.7068 | 0.69913 | 5.554 | 0.57929 | 0.76653 | 5.926 | 0.6211 | 0.79071 | 38.7552 | 0.66931 | 0.78068 | 37.6263 | 0.65271 | 0.7805 | 37.5452 | 0.65451 | 273 | 0.52831 | 0.027611 | 0.40874 | 0.0030646 | 0.94675 | 0.22385 | 0.39202 | 384.9575 | 1020.0735 | 114.1285 | 236.8482 | 342.8676 | 452.4478 | 342.2732 | 28.6422 | 37.6141 | 28.3474 | 49.5451 | 7.7097 | 0.046248 | 105.7233 | 134.8646 | 40 | 75.466 | 100.8082 | 128.3955 | 40 | 74.909 | 99.7434 | 74.876 | 180000.5 | 94.8646 | 0.73425 | 0.90406 | 179721.5 | 278.5 | 0 | 0.5 | 105.742 | 0.037523 | 0.013 | 176894.5 | 0.7181 | 0.97727 | 3106 | 1.6542 | 94.8646 | 106.4468 | 1.5963 | 278.5 | 6.1521 | 6.1863 | 6.4508 | 6.5538 | 6.1992 | 104.5439 | 6.1964 | 180000 | 88.3955 | 0.1591 | 0.19528 | 179999.5 | 0 | 0 | 0.5 | 100.8093 | 0.033447 | 0.012 | 176892 | 0.15613 | 0.20711 | 3108 | 0.32797 | 88.3955 | 101.1644 | 1.3366 | 0 | [7 empty] | 3600 | 95443.379 | inf | 95443.379 | 95443.379 | 1.1662e+28 | 47721.6895 | 94.8646 | 87.4323 | 69869.4256 | inf | 69869.4256 | 69869.4256 | 2.1741e+38 | 34934.7128 | 88.3955 | 84.1978 | Diode | 10.8954 | 7.976
Text_H100_Deepspeedds_z3 | H_100 | 3600 | 0.8033 | 1.018 | 0.18971 | 0.8033 | 1.2673 | 0.77198 | 85.6422 | 13.4328 | 536 | 1.7048 | 0.91924 | 0.20611 | 0.71313 | 35.6564 | 1.0069 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 352 | 268 | 0 | 0.80419 | 1.2171e-05 | 0.7229 | 0.28569 | 0.0092759 | 0.12383 | 0.78922 | 0.82273 | 0.82536 | 0.70356 | 0.037152 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.081189 | 0.009089 | 0.83422 | 0.82427 | 0.81209 | 0.80857 | 0.68357 | 0.44018 | 0.46108 | 0.15539 | 0.10397 | 0.10652 | 0.062593 | 0.052909 | 0.053101 | 0.79943 | 3.3657 | 0.70053 | 0.43584 | 1.5818 | 0.33461 | 0.34234 | 1.49 | 0.30116 | 0.80769 | 6.6649 | 0.68652 | 0.66948 | 5.2965 | 0.55209 | 0.76206 | 5.8457 | 0.61561 | 0.78168 | 38.131 | 0.65897 | 0.7705 | 37.1378 | 0.64273 | 0.77098 | 37.3601 | 0.64354 | 268 | 0.065105 | 0.037152 | 0.39111 | 0.006674 | 0.80098 | 0.21051 | 0.11513 | 384.0682 | 994.1323 | 113.8648 | 230.825 | 342.7504 | 439.9593 | 337.7796 | 28.6357 | 36.6025 | 27.9889 | 49.5616 | 7.7105 | 0.046232 | 105.6901 | 134.7301 | 40 | 75.413 | 100.7771 | 128.3306 | 40 | 74.9528 | 99.7125 | 74.7465 | 180000.5 | 94.7301 | 0.73397 | 0.89112 | 179732 | 268 | 0 | 0.5 | 105.7088 | 0.037311 | 0.013 | 177095.5 | 0.71924 | 0.93738 | 2905 | 1.6322 | 94.7301 | 106.2588 | 1.6913 | 268 | 6.0736 | 6.0899 | 6.3084 | 6.424 | 6.1022 | 104.255 | 6.1702 | 180000 | 88.3306 | 0.15906 | 0.19251 | 179999.5 | 0 | 0 | 0.5 | 100.7782 | 0.032754 | 0.012 | 177073 | 0.15635 | 0.20234 | 2927 | 0.32309 | 88.3306 | 101.2711 | 1.3756 | 0 | [7 empty] | 3600 | 96181.2709 | inf | 96181.2709 | 96181.2709 | 1.3646e+28 | 48090.6355 | 94.7301 | 87.365 | 70145.6149 | inf | 70145.6149 | 70145.6149 | 2.4998e+38 | 35072.8075 | 88.3306 | 84.1653 | Diode | 10.9796 | 8.0075
Text_H100_Lamma_1B | H_100 | 3600 | 0.8033 | 1.363 | 0.29308 | 0.8033 | 1.6967 | 1.0028 | 50.7711 | 4.9451 | 1423 | 2.4306 | 1.2554 | 0.34118 | 0.91426 | 45.713 | 1.341 | 2.5587 | 2.65 | 2.4997 | 2.58 | 711 | 5.0585 | 0.19477 | 716 | 711.5 | 120 | 1.0308 | 0.0025411 | 0.97753 | 0.25672 | 0.037371 | 0.55691 | 1.0177 | 1.0618 | 1.063 | 0.98388 | 0.11051 | 0 | 1.1207 | 1.447 | 95.5842 | 0.887 | 0.89019 | 0.0709 | 0.55691 | 0.0078411 | 0.8899 | 0.83294 | 0.82412 | 0.81979 | 0.907 | 0.77441 | 0.81957 | 0.35131 | 0.28246 | 0.2907 | 0.34527 | 0.26293 | 0.26956 | 1.0432 | 4.3238 | 0.95466 | 0.98434 | 3.9828 | 0.88032 | 0.99727 | 4.0471 | 0.89585 | 1.0317 | 8.6511 | 0.9518 | 0.98856 | 7.998 | 0.88399 | 0.99984 | 8.1218 | 0.8983 | 1.0094 | 49.4873 | 0.91115 | 1.0026 | 48.3253 | 0.892 | 1.002 | 48.8175 | 0.89749 | 5 | 0.41701 | 0.095943 | 0.25732 | 0.025958 | 1.1806 | 0.30359 | 0.34203 | 409.7009 | 1331.021 | 121.4641 | 309.0463 | 346.2375 | 606.1321 | 454.7578 | 28.8309 | 49.9624 | 37.2524 | 49.075 | 7.6868 | 0.046691 | 106.3654 | 138.2622 | 40 | 76.862 | 101.3986 | 129.6668 | 40 | 75.3885 | 100.327 | 75.338 | 180000.5 | 98.2622 | 0.74215 | 1.2313 | 179289 | 711 | 0 | 0.5 | 106.3847 | 0.031859 | 0.013 | 178780 | 0.7108 | 1.2985 | 1220.5 | 5.3355 | 98.2622 | 108.0861 | 3.2885 | 711 | 8.1963 | 8.2075 | 8.4493 | 8.945 | 8.2204 | 106.6402 | 2.9894 | 180000 | 89.6668 | 0.16019 | 0.26333 | 179999.5 | 0 | 0 | 0.5 | 101.3998 | 0.031327 | 0.012 | 178813.5 | 0.15458 | 0.27517 | 1186.5 | 1.0063 | 89.6668 | 102.9954 | 3.2546 | 0 | [7 empty] | 3600 | 78804.133 | inf | 78804.133 | 78804.133 | 8.9893e+25 | 39402.0705 | 98.2622 | 89.1311 | 64707.4012 | inf | 64707.4012 | 64707.4012 | 3.1467e+36 | 32353.7006 | 89.6668 | 84.8334 | Diode | 8.9959 | 7.3867
Text_H100_Lamma_3B | H_100 | 3600 | 0.8033 | 1.1542 | 0.22271 | 0.8033 | 1.4368 | 0.86997 | 72.2444 | 8.2569 | 856 | 1.9553 | 1.0578 | 0.23324 | 0.82456 | 41.2281 | 1.1347 | 6.0707 | 6.26 | 2.345 | 2.36 | 427 | 8.4043 | 0.20018 | 428 | 427.5 | 0 | 0.90821 | 0.00015446 | 0.85675 | 0.32197 | 0.054197 | 0.29943 | 0.87656 | 0.92285 | 0.92296 | 0.85914 | 0.18832 | 0 | 3.4802 | 3.5882 | 90.8855 | 1.6989 | 0.29457 | 0.052616 | 0.29826 | 0.00069069 | 0.86547 | 0.84165 | 0.82368 | 0.82435 | 0.76455 | 0.55552 | 0.5777 | 0.19763 | 0.13655 | 0.14064 | 0.09049 | 0.069116 | 0.069318 | 0.90299 | 4.2365 | 0.87887 | 0.72406 | 2.8271 | 0.60745 | 0.84762 | 2.908 | 0.64416 | 0.8947 | 7.7614 | 0.8243 | 0.85543 | 6.9338 | 0.74265 | 0.86644 | 7.1447 | 0.7584 | 0.87751 | 43.5655 | 0.77258 | 0.86944 | 41.9074 | 0.75199 | 0.87131 | 42.4168 | 0.75762 | 429 | 0.22252 | 0.16161 | 0.52293 | 0.03895 | 1.0403 | 0.24441 | 0.18343 | 398.455 | 1127.1708 | 118.1301 | 261.7149 | 344.6799 | 504.5485 | 385.9062 | 28.7437 | 41.8206 | 31.8356 | 49.2912 | 7.6973 | 0.046486 | 106.1997 | 136.2705 | 40 | 76.1011 | 101.2568 | 128.9297 | 40 | 75.3 | 100.1881 | 75.3141 | 180000.5 | 96.2705 | 0.7385 | 1.0253 | 179573 | 427 | 0 | 0.5 | 106.2188 | 0.034455 | 0.013 | 177431 | 0.71941 | 1.0764 | 2569.5 | 2.0568 | 96.2705 | 107.5424 | 1.712 | 427 | 6.9727 | 6.9724 | 7.221 | 8.0265 | 7.0031 | 105.3293 | 4.607 | 180000 | 88.9297 | 0.15969 | 0.22047 | 179999.5 | 0 | 0 | 0.5 | 101.258 | 0.03267 | 0.012 | 177521.5 | 0.15622 | 0.23268 | 2478.5 | 0.40817 | 88.9297 | 102.3246 | 1.6148 | 0 | [7 empty] | 3600 | 88114.0389 | inf | 88114.0389 | 88114.0389 | 1.3863e+27 | 44057.0196 | 96.2705 | 88.1353 | 67647.12 | inf | 67647.12 | 67647.12 | 3.3125e+37 | 33823.56 | 88.9297 | 84.4649 | Diode | 10.0587 | 7.7223
Text_H100_Lamma_8B | H_100 | 3600 | 0.8033 | 1.018 | 0.18971 | 0.8033 | 1.2673 | 0.77198 | 85.6422 | 13.4328 | 536 | 1.7048 | 0.91924 | 0.20611 | 0.71313 | 35.6564 | 1.0069 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 352 | 268 | 0 | 0.80419 | 1.2171e-05 | 0.7229 | 0.28569 | 0.0092759 | 0.12383 | 0.78922 | 0.82273 | 0.82536 | 0.70356 | 0.037152 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.081189 | 0.009089 | 0.83422 | 0.82427 | 0.81209 | 0.80857 | 0.68357 | 0.44018 | 0.46108 | 0.15539 | 0.10397 | 0.10652 | 0.062593 | 0.052909 | 0.053101 | 0.79943 | 3.3657 | 0.70053 | 0.43584 | 1.5818 | 0.33461 | 0.34234 | 1.49 | 0.30116 | 0.80769 | 6.6649 | 0.68652 | 0.66948 | 5.2965 | 0.55209 | 0.76206 | 5.8457 | 0.61561 | 0.78168 | 38.131 | 0.65897 | 0.7705 | 37.1378 | 0.64273 | 0.77098 | 37.3601 | 0.64354 | 268 | 0.065105 | 0.037152 | 0.39111 | 0.006674 | 0.80098 | 0.21051 | 0.11513 | 384.0682 | 994.1323 | 113.8648 | 230.825 | 342.7504 | 439.9593 | 337.7796 | 28.6357 | 36.6025 | 27.9889 | 49.5616 | 7.7105 | 0.046232 | 105.6901 | 134.7301 | 40 | 75.413 | 100.7771 | 128.3306 | 40 | 74.9528 | 99.7125 | 74.7465 | 180000.5 | 94.7301 | 0.73397 | 0.89112 | 179732 | 268 | 0 | 0.5 | 105.7088 | 0.037311 | 0.013 | 177095.5 | 0.71924 | 0.93738 | 2905 | 1.6322 | 94.7301 | 106.2588 | 1.6913 | 268 | 6.0736 | 6.0899 | 6.3084 | 6.424 | 6.1022 | 104.255 | 6.1702 | 180000 | 88.3306 | 0.15906 | 0.19251 | 179999.5 | 0 | 0 | 0.5 | 100.7782 | 0.032754 | 0.012 | 177073 | 0.15635 | 0.20234 | 2927 | 0.32309 | 88.3306 | 101.2711 | 1.3756 | 0 | [7 empty] | 3600 | 96181.2709 | inf | 96181.2709 | 96181.2709 | 1.3646e+28 | 48090.6355 | 94.7301 | 87.365 | 70145.6149 | inf | 70145.6149 | 70145.6149 | 2.4998e+38 | 35072.8075 | 88.3306 | 84.1653 | Diode | 10.9796 | 8.0075
Text_H100_SeqLength_1024 | H_100 | 3600 | 0.8033 | 1.0231 | 0.18862 | 0.8033 | 1.2736 | 0.77154 | 85.7133 | 6.6667 | 544 | 1.5805 | 0.91929 | 0.21004 | 0.70925 | 35.4624 | 1.0083 | 11.3757 | 11.62 | 1.8841 | 2.14 | 271 | 13.2338 | 0.064134 | 392 | 271.5 | 0 | 0.80884 | 1.1857e-05 | 0.7181 | 0.28315 | 0.010524 | 0.12108 | 0.79111 | 0.8275 | 0.82915 | 0.69608 | 0.032796 | 0 | 0.15489 | 44.8184 | 52.5946 | 1.9177 | 0.42111 | 0.093287 | 0.036966 | -0.01223 | 0.8339 | 0.82816 | 0.81446 | 0.81143 | 0.69548 | 0.42843 | 0.45648 | 0.15639 | 0.10453 | 0.10714 | 0.063162 | 0.054555 | 0.054592 | 0.80016 | 3.147 | 0.66643 | 0.43832 | 1.5967 | 0.33733 | 0.35673 | 1.5263 | 0.30863 | 0.80099 | 6.3594 | 0.66745 | 0.65128 | 5.1281 | 0.53507 | 0.76042 | 5.8282 | 0.61254 | 0.78086 | 38.0936 | 0.65619 | 0.77071 | 37.1453 | 0.64263 | 0.76968 | 37.063 | 0.64289 | 272 | 0.042553 | 0.028021 | 0.3843 | 0.0067453 | 0.80223 | 0.20597 | 0.11951 | 383.9183 | 999.1236 | 113.8204 | 231.9839 | 342.7306 | 442.3582 | 337.5914 | 28.6346 | 36.7969 | 27.9733 | 49.5644 | 7.7106 | 0.04623 | 105.6888 | 134.7652 | 40 | 75.5204 | 100.776 | 128.3738 | 40 | 75.1389 | 99.7115 | 74.99 | 180000.5 | 94.7652 | 0.73392 | 0.89106 | 179728 | 272 | 0 | 0.5 | 105.7075 | 0.037258 | 0.013 | 177102 | 0.71897 | 0.94049 | 2898.5 | 1.6478 | 94.7652 | 105.9474 | 1.6926 | 272 | 6.0631 | 6.0809 | 6.3077 | 6.4292 | 6.0934 | 104.2984 | 6.0971 | 180000 | 88.3738 | 0.15905 | 0.1925 | 179999.5 | 0 | 0 | 0.5 | 100.7771 | 0.032828 | 0.012 | 177106.5 | 0.15631 | 0.20303 | 2893.5 | 0.32711 | 88.3738 | 101.4652 | 1.3971 | 0 | [7 empty] | 3600 | 95988.0613 | inf | 95988.0613 | 95988.0613 | 1.3696e+28 | 47994.0307 | 94.7652 | 87.3826 | 69961.8755 | inf | 69961.8755 | 69961.8755 | 2.5071e+38 | 34980.9377 | 88.3738 | 84.1869 | Diode | 10.9575 | 7.9865
Text_H100_SeqLength_2048 | H_100 | 3600 | 0.8033 | 1.018 | 0.18971 | 0.8033 | 1.2673 | 0.77198 | 85.6422 | 13.4328 | 536 | 1.7048 | 0.91924 | 0.20611 | 0.71313 | 35.6564 | 1.0069 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 352 | 268 | 0 | 0.80419 | 1.2171e-05 | 0.7229 | 0.28569 | 0.0092759 | 0.12383 | 0.78922 | 0.82273 | 0.82536 | 0.70356 | 0.037152 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.081189 | 0.009089 | 0.83422 | 0.82427 | 0.81209 | 0.80857 | 0.68357 | 0.44018 | 0.46108 | 0.15539 | 0.10397 | 0.10652 | 0.062593 | 0.052909 | 0.053101 | 0.79943 | 3.3657 | 0.70053 | 0.43584 | 1.5818 | 0.33461 | 0.34234 | 1.49 | 0.30116 | 0.80769 | 6.6649 | 0.68652 | 0.66948 | 5.2965 | 0.55209 | 0.76206 | 5.8457 | 0.61561 | 0.78168 | 38.131 | 0.65897 | 0.7705 | 37.1378 | 0.64273 | 0.77098 | 37.3601 | 0.64354 | 268 | 0.065105 | 0.037152 | 0.39111 | 0.006674 | 0.80098 | 0.21051 | 0.11513 | 384.0682 | 994.1323 | 113.8648 | 230.825 | 342.7504 | 439.9593 | 337.7796 | 28.6357 | 36.6025 | 27.9889 | 49.5616 | 7.7105 | 0.046232 | 105.6901 | 134.7301 | 40 | 75.413 | 100.7771 | 128.3306 | 40 | 74.9528 | 99.7125 | 74.7465 | 180000.5 | 94.7301 | 0.73397 | 0.89112 | 179732 | 268 | 0 | 0.5 | 105.7088 | 0.037311 | 0.013 | 177095.5 | 0.71924 | 0.93738 | 2905 | 1.6322 | 94.7301 | 106.2588 | 1.6913 | 268 | 6.0736 | 6.0899 | 6.3084 | 6.424 | 6.1022 | 104.255 | 6.1702 | 180000 | 88.3306 | 0.15906 | 0.19251 | 179999.5 | 0 | 0 | 0.5 | 100.7782 | 0.032754 | 0.012 | 177073 | 0.15635 | 0.20234 | 2927 | 0.32309 | 88.3306 | 101.2711 | 1.3756 | 0 | [7 empty] | 3600 | 96181.2709 | inf | 96181.2709 | 96181.2709 | 1.3646e+28 | 48090.6355 | 94.7301 | 87.365 | 70145.6149 | inf | 70145.6149 | 70145.6149 | 2.4998e+38 | 35072.8075 | 88.3306 | 84.1653 | Diode | 10.9796 | 8.0075
Text_H100_SeqLength_4096 | H_100 | 3600 | 0.8033 | 1.0237 | 0.19052 | 0.8033 | 1.2744 | 0.7737 | 85.56 | 13.4328 | 536 | 1.6363 | 0.9219 | 0.20549 | 0.71641 | 35.8205 | 1.0093 | 11.4909 | 11.72 | 1.9346 | 2.08 | 267 | 13.41 | 0.02735 | 420 | 268 | 0 | 0.81203 | 1.2868e-05 | 0.72564 | 0.29004 | 0.0082579 | 0.13842 | 0.79635 | 0.82771 | 0.82789 | 0.70697 | 0.035656 | 0 | 0.052026 | 45.5774 | 51.8231 | 2.0413 | 0.41035 | 0.095876 | 0.023626 | 0.0046555 | 0.83466 | 0.8248 | 0.81082 | 0.80848 | 0.67042 | 0.43573 | 0.4561 | 0.1579 | 0.1063 | 0.10889 | 0.061896 | 0.054168 | 0.054371 | 0.80222 | 3.2694 | 0.69039 | 0.43037 | 1.5561 | 0.32943 | 0.34375 | 1.4764 | 0.29688 | 0.80657 | 6.8827 | 0.70781 | 0.65569 | 5.1634 | 0.53915 | 0.76454 | 5.8831 | 0.61735 | 0.78424 | 38.2826 | 0.66174 | 0.77305 | 37.2604 | 0.64519 | 0.77337 | 37.5562 | 0.64745 | 268 | 0.05722 | 0.034566 | 0.39585 | 0.0054886 | 0.8125 | 0.21054 | 0.11812 | 384.2681 | 999.7159 | 113.9241 | 232.1214 | 342.7767 | 442.643 | 338.6062 | 28.6371 | 36.82 | 28.0555 | 49.5579 | 7.7103 | 0.046236 | 105.6983 | 134.765 | 40 | 75.4479 | 100.7848 | 128.3566 | 40 | 74.9999 | 99.7202 | 74.8206 | 180000.5 | 94.765 | 0.73403 | 0.89338 | 179732 | 268 | 0 | 0.5 | 105.717 | 0.037199 | 0.013 | 177122.5 | 0.71908 | 0.94071 | 2878 | 1.6542 | 94.765 | 106.086 | 1.7013 | 268 | 6.0927 | 6.1022 | 6.3314 | 6.4255 | 6.1197 | 104.2851 | 6.1357 | 180000 | 88.3566 | 0.15907 | 0.19299 | 179999.5 | 0 | 0 | 0.5 | 100.7859 | 0.032863 | 0.012 | 177100 | 0.15632 | 0.20308 | 2900 | 0.32702 | 88.3566 | 101.6835 | 1.3958 | 0 | [7 empty] | 3600 | 95988.6881 | inf | 95988.6881 | 95988.6881 | 1.3138e+28 | 47994.344 | 94.765 | 87.3825 | 70035.1375 | inf | 70035.1375 | 70035.1375 | 2.417e+38 | 35017.5687 | 88.3566 | 84.1783 | Diode | 10.9576 | 7.9949
Image_B200_BatchSize_128 | B_200 | 3600 | 0.8033 | 1.4935 | 0.49334 | 0.8033 | 1.8592 | 0.97643 | 30.1867 | 11.3924 | 632 | 1.8688 | 1.4602 | 0.50136 | 0.95879 | 47.9397 | 1.4895 | 3.422 | 3.48 | 7.9642 | 8.78 | 316 | 11.3863 | 0.05211 | 316 | 316 | 0 | 0.99473 | 0.00097525 | 0.97287 | 0.50794 | 0.014234 | 0.1402 | 0.9547 | 0.99602 | 0.99827 | 0.97175 | 0.043117 | 0 | 0.047497 | 73.9386 | 25.4308 | 0.50986 | 0.058211 | 0.014977 | 0.082049 | -0.016191 | 0.89747 | 0.8431 | 0.81738 | 0.81107 | 0.86701 | 0.90155 | 0.93311 | 0.15329 | 0.15111 | 0.15409 | 0.019614 | 0.018931 | 0.018931 | 0.99182 | 5.717 | 1.2012 | 0.70379 | 3.1637 | 0.68415 | 0.9342 | 3.8098 | 0.85571 | 0.98787 | 8.3786 | 0.93016 | 0.97316 | 7.8192 | 0.87176 | 0.97482 | 8.1026 | 0.90288 | 0.98142 | 48.5719 | 0.90461 | 0.97519 | 47.0025 | 0.87507 | 0.97521 | 46.796 | 0.87184 | 316 | 0.061526 | 0.041158 | 0.79884 | 0.0040458 | 0.8161 | 0.15872 | 0.092371 | 413.1867 | 1458.5026 | 122.4976 | 338.6459 | 346.7291 | 671.2682 | 455.8769 | 28.8584 | 55.1442 | 37.0047 | 49.0072 | 7.6835 | 0.046755 | 106.4341 | 140.1928 | 40 | 77.3745 | 101.4596 | 130.188 | 40 | 75.8499 | 100.387 | 75.6287 | 180000.5 | 100.1928 | 0.74331 | 1.4213 | 179684.5 | 315.5 | 0 | 0.5 | 106.4535 | 0.030984 | 0.013 | 179136 | 0.72906 | 1.4419 | 864.5 | 3.6954 | 100.1928 | 106.8379 | 4.3767 | 315.5 | 8.534 | 8.5452 | 8.713 | 8.7749 | 8.5451 | 108.2112 | 5.7563 | 180000 | 90.188 | 0.16035 | 0.30178 | 179999.5 | 0 | 0 | 0.5 | 101.4608 | 0.029214 | 0.012 | 179132.5 | 0.15792 | 0.30582 | 867.5 | 0.66374 | 90.188 | 107.4114 | 3.8436 | 0 | [7 empty] | 3600 | 70847.713 | inf | 70847.713 | 70847.713 | 7.8377e+24 | 35423.8598 | 100.1928 | 90.0964 | 62720.1022 | inf | 62720.1022 | 62720.1022 | 3.9682e+35 | 31360.0511 | 90.188 | 85.094 | Diode | 8.0876 | 7.1598
Image_B200_BatchSize_256 | B_200 | 3600 | 0.8033 | 1.7263 | 0.49824 | 0.8033 | 2.149 | 1.1885 | 23.8711 | 11.1111 | 647 | 2.3716 | 1.678 | 0.50382 | 1.1742 | 58.708 | 1.7052 | 2.6435 | 2.68 | 8.4886 | 9.28 | 323 | 11.1321 | 0.072785 | 323.5 | 323.5 | 323.5 | 1.2053 | 0.032033 | 1.18 | 0.53287 | 0.014925 | 1.1938 | 1.1938 | 1.2258 | 1.2266 | 1.1801 | 0.054767 | 0 | 0.032596 | 62.7865 | 35.5695 | 1.4669 | 0.10555 | 0.038932 | 1.1925 | 0.024075 | 0.91929 | 0.83831 | 0.81838 | 0.81395 | 1.0463 | 1.1918 | 1.2406 | 0.1911 | 0.20786 | 0.21311 | 0.034417 | 0.023579 | 0.023588 | 1.2032 | 6.9161 | 1.4957 | 0.77934 | 3.6564 | 0.80707 | 1.1187 | 4.4701 | 1.0104 | 1.2031 | 10.1176 | 1.1505 | 1.1746 | 9.4557 | 1.0797 | 1.1871 | 9.8459 | 1.1284 | 1.1918 | 59.499 | 1.1331 | 1.1879 | 57.2552 | 1.0917 | 1.1889 | 56.3409 | 1.074 | 321 | 0.88968 | 0.054767 | 0.78975 | 0.0044524 | 1.4283 | 0.32049 | 0.64936 | 423.2325 | 1685.8082 | 125.4759 | 391.4234 | 348.1692 | 790.4809 | 564.2375 | 28.939 | 64.5554 | 45.5654 | 48.8096 | 7.6739 | 0.046945 | 106.7107 | 142.3546 | 40 | 77.8207 | 101.7143 | 130.7705 | 40 | 76.1797 | 100.6388 | 76.0542 | 180000.5 | 102.3546 | 0.74669 | 1.6565 | 179677 | 0 | 323 | 0.5 | 106.7303 | 0.030843 | 0.013 | 179139 | 0.72917 | 1.6816 | 861.5 | 4.3899 | 102.3546 | 106.0968 | 4.3807 | 323 | 10.4459 | 10.4673 | 10.5949 | 10.7 | 10.4545 | 109.4336 | 5.5578 | 180000 | 90.7705 | 0.16082 | 0.34965 | 179999.5 | 0 | 0 | 0.5 | 101.7155 | 0.02924 | 0.012 | 178992.5 | 0.15775 | 0.35462 | 1007.5 | 0.706 | 90.7705 | 107.2718 | 3.3104 | 0 | [7 empty] | 3600 | 63013.0231 | inf | 63013.0231 | 63013.0231 | 7.4726e+23 | 31506.5876 | 102.3546 | 91.1773 | 60581.6307 | inf | 60581.6307 | 60581.6307 | 5.3596e+34 | 30290.8154 | 90.7705 | 85.3853 | Diode | 7.1933 | 6.9157
Image_B200_BatchSize_512 | B_200 | 3600 | 0.8033 | 1.8597 | 0.4951 | 0.8033 | 2.315 | 1.3309 | 20.5644 | 11.1111 | 656 | 2.7176 | 1.8118 | 0.50181 | 1.31 | 65.5007 | 1.8527 | 2.2571 | 2.3 | 8.7276 | 9.1 | 328 | 10.9847 | 0.035334 | 328 | 328 | 328 | 1.3506 | 0.24452 | 1.3088 | 0.5284 | 0.014771 | 0.18328 | 1.307 | 1.3615 | 1.3615 | 1.3031 | 0.054536 | 0 | 0.018962 | 57.9039 | 40.8257 | 1.1347 | 0.090152 | 0.026503 | 0.0039665 | 0.023539 | 0.92846 | 0.8345 | 0.81617 | 0.81241 | 1.1707 | 1.4343 | 1.496 | 0.22239 | 0.25706 | 0.2642 | 0.047443 | 0.034691 | 0.034697 | 1.3518 | 7.6433 | 1.6812 | 0.84369 | 3.997 | 0.8941 | 1.2178 | 5.2302 | 1.2057 | 1.3474 | 11.2343 | 1.2924 | 1.3094 | 10.548 | 1.2173 | 1.3302 | 10.9821 | 1.2711 | 1.337 | 66.5981 | 1.2821 | 1.3305 | 64.1301 | 1.235 | 1.3307 | 64.171 | 1.2311 | 328 | 0.10548 | 0.052886 | 0.77037 | 0.0073462 | 1.3463 | 0.26346 | 0.10329 | 427.453 | 1816.0735 | 126.7271 | 421.6694 | 348.7845 | 860.5742 | 638.521 | 28.9734 | 70.0481 | 51.3986 | 48.7256 | 7.6698 | 0.047025 | 106.8161 | 143.971 | 40 | 77.7274 | 101.81 | 131.1883 | 40 | 76.2597 | 100.7332 | 75.9651 | 180000.5 | 103.971 | 0.74814 | 1.8122 | 179672.5 | 0 | 327.5 | 0.5 | 106.8358 | 0.031967 | 0.013 | 178834.5 | 0.7277 | 1.8501 | 1166 | 3.8826 | 103.971 | 106.7264 | 3.4485 | 327.5 | 11.786 | 11.8061 | 11.9565 | 12.0427 | 11.7944 | 110.142 | 5.6383 | 180000 | 91.1883 | 0.16102 | 0.38122 | 179999.5 | 0 | 0 | 0.5 | 101.8111 | 0.030267 | 0.012 | 178677 | 0.15747 | 0.38824 | 1323 | 0.64123 | 91.1883 | 105.2522 | 2.6777 | 0 | [7 empty] | 3600 | 57801.2511 | inf | 57801.2511 | 57801.2511 | 1.9813e+23 | 28901.0663 | 103.971 | 91.9855 | 59100.0342 | inf | 59100.0342 | 59100.0342 | 1.7521e+34 | 29550.0171 | 91.1883 | 85.5942 | IGBT | 6.5983 | 6.7466
Image_B200_ImageSize_32 | B_200 | 3600 | 0.8033 | 1.4935 | 0.49334 | 0.8033 | 1.8592 | 0.97643 | 30.1867 | 11.3924 | 632 | 1.8688 | 1.4602 | 0.50136 | 0.95879 | 47.9397 | 1.4895 | 3.422 | 3.48 | 7.9642 | 8.78 | 316 | 11.3863 | 0.05211 | 316 | 316 | 0 | 0.99473 | 0.00097525 | 0.97287 | 0.50794 | 0.014234 | 0.1402 | 0.9547 | 0.99602 | 0.99827 | 0.97175 | 0.043117 | 0 | 0.047497 | 73.9386 | 25.4308 | 0.50986 | 0.058211 | 0.014977 | 0.082049 | -0.016191 | 0.89747 | 0.8431 | 0.81738 | 0.81107 | 0.86701 | 0.90155 | 0.93311 | 0.15329 | 0.15111 | 0.15409 | 0.019614 | 0.018931 | 0.018931 | 0.99182 | 5.717 | 1.2012 | 0.70379 | 3.1637 | 0.68415 | 0.9342 | 3.8098 | 0.85571 | 0.98787 | 8.3786 | 0.93016 | 0.97316 | 7.8192 | 0.87176 | 0.97482 | 8.1026 | 0.90288 | 0.98142 | 48.5719 | 0.90461 | 0.97519 | 47.0025 | 0.87507 | 0.97521 | 46.796 | 0.87184 | 316 | 0.061526 | 0.041158 | 0.79884 | 0.0040458 | 0.8161 | 0.15872 | 0.092371 | 413.1867 | 1458.5026 | 122.4976 | 338.6459 | 346.7291 | 671.2682 | 455.8769 | 28.8584 | 55.1442 | 37.0047 | 49.0072 | 7.6835 | 0.046755 | 106.4341 | 140.1928 | 40 | 77.3745 | 101.4596 | 130.188 | 40 | 75.8499 | 100.387 | 75.6287 | 180000.5 | 100.1928 | 0.74331 | 1.4213 | 179684.5 | 315.5 | 0 | 0.5 | 106.4535 | 0.030984 | 0.013 | 179136 | 0.72906 | 1.4419 | 864.5 | 3.6954 | 100.1928 | 106.8379 | 4.3767 | 315.5 | 8.534 | 8.5452 | 8.713 | 8.7749 | 8.5451 | 108.2112 | 5.7563 | 180000 | 90.188 | 0.16035 | 0.30178 | 179999.5 | 0 | 0 | 0.5 | 101.4608 | 0.029214 | 0.012 | 179132.5 | 0.15792 | 0.30582 | 867.5 | 0.66374 | 90.188 | 107.4114 | 3.8436 | 0 | [7 empty] | 3600 | 70847.713 | inf | 70847.713 | 70847.713 | 7.8377e+24 | 35423.8598 | 100.1928 | 90.0964 | 62720.1022 | inf | 62720.1022 | 62720.1022 | 3.9682e+35 | 31360.0511 | 90.188 | 85.094 | Diode | 8.0876 | 7.1598
Image_B200_ImageSize_64 | B_200 | 3600 | 0.8033 | 1.2394 | 0.32021 | 0.8033 | 1.5429 | 0.88915 | 52.9178 | 18.3673 | 392 | 1.6369 | 1.2062 | 0.32994 | 0.87627 | 43.8133 | 1.2244 | 9.7012 | 9.78 | 8.6651 | 9.1 | 196 | 18.3664 | 0.023299 | 200 | 195.5 | 0 | 0.90474 | 0.00011944 | 0.88835 | 0.70567 | 0.023076 | 0.21525 | 0.86593 | 0.91201 | 0.91389 | 0.88783 | 0.081374 | 0 | 0.023059 | 87.7175 | 11.8978 | 0.31887 | 0.032617 | 0.010097 | 0.21524 | 0.044598 | 0.90179 | 0.8538 | 0.81585 | 0.81763 | 0.76987 | 0.62732 | 0.64938 | 0.090059 | 0.07021 | 0.071961 | 0.0093193 | 0.0097672 | 0.0097672 | 0.89773 | 4.6531 | 0.96687 | 0.43356 | 1.6888 | 0.36587 | 0.38725 | 1.1806 | 0.24629 | 0.89535 | 9.6889 | 0.99799 | 0.84163 | 6.6362 | 0.73049 | 0.88388 | 6.6667 | 0.75954 | 0.89104 | 45.0897 | 0.83193 | 0.88882 | 42.8394 | 0.80124 | 0.88957 | 42.482 | 0.79541 | 392 | 0.16137 | 0.078068 | 0.88198 | 0.021021 | 0.64197 | 0.12331 | 0.073319 | 415.1771 | 1210.3467 | 123.0877 | 281.0273 | 347.0117 | 545.6148 | 401.2265 | 28.8742 | 45.1213 | 32.9188 | 48.9683 | 7.6816 | 0.046792 | 106.5566 | 137.9535 | 40 | 77.5536 | 101.5776 | 129.852 | 40 | 75.6705 | 100.5043 | 75.8131 | 180000.5 | 97.9535 | 0.74397 | 1.1463 | 179804.5 | 195.5 | 0 | 0.5 | 106.576 | 0.029839 | 0.013 | 178539.5 | 0.73465 | 1.1597 | 1461 | 1.883 | 97.9535 | 110.7493 | 2.3495 | 195.5 | 7.5248 | 7.5463 | 7.6736 | 7.7559 | 7.5366 | 106.5435 | 6.4495 | 180000 | 89.852 | 0.16045 | 0.24514 | 179999.5 | 0 | 0 | 0.5 | 101.5787 | 0.027462 | 0.012 | 179319 | 0.15905 | 0.24774 | 681 | 0.52808 | 89.852 | 104.7089 | 4.3818 | 0 | [7 empty] | 3600 | 80169.1372 | inf | 80169.1372 | 80169.1372 | 1.4057e+26 | 40084.5689 | 97.9535 | 88.9768 | 63992.9835 | inf | 63992.9835 | 63992.9835 | 4.5082e+36 | 31996.4918 | 89.852 | 84.926 | Diode | 9.1517 | 7.3051
Image_B200_ImageSize_128 | B_200 | 3600 | 0.8033 | 0.921 | 0.25436 | 0.8033 | 1.1465 | 0.6465 | 86.0489 | 69.2308 | 112 | 0.85685 | 0.88477 | 0.26134 | 0.62343 | 31.1714 | 0.91732 | 54.9415 | 60.06 | 9.5057 | 11.06 | 55 | 63.98 | 0.28196 | 56 | 52 | 0 | 0.64656 | 9.1424e-08 | 0.63237 | 0.48386 | 0.028525 | 0.095732 | 0.61038 | 0.65784 | 0.6627 | 0.63097 | 0.094042 | 0 | 31.9189 | 60.8605 | 6.6043 | 0.24406 | 0.18916 | 0.18309 | 0.0062691 | -0.010155 | 0.82667 | 0.88459 | 0.82734 | 0.81293 | 0.55183 | 0.33587 | 0.34989 | 0.05452 | 0.041818 | 0.04203 | 0.04367 | 0.038349 | 0.038353 | 0.6472 | 2.3018 | 0.4889 | 0.12109 | 0.41273 | 0.085471 | 0.044688 | 0.19705 | 0.039415 | 0.64975 | 5.1962 | 0.53652 | 0.19058 | 1.2534 | 0.13069 | 0.045009 | 0.39791 | 0.039795 | 0.6499 | 31.3814 | 0.53714 | 0.56718 | 27.0006 | 0.46472 | 0.64689 | 30.6969 | 0.52835 | 116 | 0.033699 | 0.091933 | 0.5973 | 0.017776 | 0.47467 | 0.089711 | 0.046586 | 380.5889 | 899.4174 | 112.8333 | 208.8334 | 342.2944 | 394.7977 | 282.9049 | 28.6101 | 32.9336 | 23.4412 | 49.626 | 7.7136 | 0.046172 | 105.631 | 134.1233 | 40 | 75.4961 | 100.725 | 128.2355 | 40 | 74.9957 | 99.6613 | 74.9943 | 180000.5 | 94.1233 | 0.73289 | 0.82509 | 179948 | 52 | 0 | 0.5 | 105.6497 | 0.037716 | 0.013 | 174454.5 | 0.72465 | 0.83488 | 5546 | 0.99227 | 94.1233 | 105.0629 | 0.90703 | 52 | 5.3496 | 5.3873 | 5.5121 | 5.5244 | 5.3688 | 104.2351 | 7.871 | 180000 | 88.2355 | 0.15891 | 0.17891 | 179999.5 | 0 | 0 | 0.5 | 100.7261 | 0.03146 | 0.012 | 173689 | 0.15726 | 0.18106 | 6311 | 0.20438 | 88.2355 | 102.5588 | 0.6087 | 0 | [7 empty] | 3600 | 99593.2749 | inf | 99593.2749 | 99593.2749 | 2.9466e+28 | 49796.6374 | 94.1233 | 87.0617 | 70553.4738 | inf | 70553.4738 | 70553.4738 | 4.9176e+38 | 35276.7369 | 88.2355 | 84.1177 | Diode | 11.3691 | 8.054
Image_B200_ModelSize_128 | B_200 | 3600 | 0.8033 | 1.4935 | 0.49334 | 0.8033 | 1.8592 | 0.97643 | 30.1867 | 11.3924 | 632 | 1.8688 | 1.4602 | 0.50136 | 0.95879 | 47.9397 | 1.4895 | 3.422 | 3.48 | 7.9642 | 8.78 | 316 | 11.3863 | 0.05211 | 316 | 316 | 0 | 0.99473 | 0.00097525 | 0.97287 | 0.50794 | 0.014234 | 0.1402 | 0.9547 | 0.99602 | 0.99827 | 0.97175 | 0.043117 | 0 | 0.047497 | 73.9386 | 25.4308 | 0.50986 | 0.058211 | 0.014977 | 0.082049 | -0.016191 | 0.89747 | 0.8431 | 0.81738 | 0.81107 | 0.86701 | 0.90155 | 0.93311 | 0.15329 | 0.15111 | 0.15409 | 0.019614 | 0.018931 | 0.018931 | 0.99182 | 5.717 | 1.2012 | 0.70379 | 3.1637 | 0.68415 | 0.9342 | 3.8098 | 0.85571 | 0.98787 | 8.3786 | 0.93016 | 0.97316 | 7.8192 | 0.87176 | 0.97482 | 8.1026 | 0.90288 | 0.98142 | 48.5719 | 0.90461 | 0.97519 | 47.0025 | 0.87507 | 0.97521 | 46.796 | 0.87184 | 316 | 0.061526 | 0.041158 | 0.79884 | 0.0040458 | 0.8161 | 0.15872 | 0.092371 | 413.1867 | 1458.5026 | 122.4976 | 338.6459 | 346.7291 | 671.2682 | 455.8769 | 28.8584 | 55.1442 | 37.0047 | 49.0072 | 7.6835 | 0.046755 | 106.4341 | 140.1928 | 40 | 77.3745 | 101.4596 | 130.188 | 40 | 75.8499 | 100.387 | 75.6287 | 180000.5 | 100.1928 | 0.74331 | 1.4213 | 179684.5 | 315.5 | 0 | 0.5 | 106.4535 | 0.030984 | 0.013 | 179136 | 0.72906 | 1.4419 | 864.5 | 3.6954 | 100.1928 | 106.8379 | 4.3767 | 315.5 | 8.534 | 8.5452 | 8.713 | 8.7749 | 8.5451 | 108.2112 | 5.7563 | 180000 | 90.188 | 0.16035 | 0.30178 | 179999.5 | 0 | 0 | 0.5 | 101.4608 | 0.029214 | 0.012 | 179132.5 | 0.15792 | 0.30582 | 867.5 | 0.66374 | 90.188 | 107.4114 | 3.8436 | 0 | [7 empty] | 3600 | 70847.713 | inf | 70847.713 | 70847.713 | 7.8377e+24 | 35423.8598 | 100.1928 | 90.0964 | 62720.1022 | inf | 62720.1022 | 62720.1022 | 3.9682e+35 | 31360.0511 | 90.188 | 85.094 | Diode | 8.0876 | 7.1598
Image_B200_ModelSize_256 | B_200 | 3600 | 0.8033 | 1.6961 | 0.44044 | 0.8033 | 2.1114 | 1.2325 | 27.96 | 21.9512 | 327 | 2.0857 | 1.6661 | 0.44722 | 1.2188 | 60.9425 | 1.6916 | 6.1114 | 6.18 | 15.8861 | 16.66 | 163 | 21.9975 | 0.065551 | 163.5 | 163.5 | 163.5 | 1.2507 | 0.03305 | 1.2313 | 0.9467 | 0.032521 | 1.2173 | 1.2223 | 1.2489 | 1.2522 | 1.2302 | 0.10104 | 0 | 0.12012 | 89.9932 | 9.417 | 0.39017 | 0.055105 | 0.02448 | 1.2173 | 0.027752 | 0.95315 | 0.88011 | 0.83607 | 0.81556 | 1.0755 | 1.1911 | 1.2438 | 0.10312 | 0.1092 | 0.1119 | 0.0063451 | 0.0080583 | 0.0080583 | 1.2426 | 9.0293 | 1.8762 | 0.50466 | 2.6729 | 0.5776 | 0.15396 | 0.42127 | 0.085127 | 1.243 | 15.1099 | 1.6396 | 0.84563 | 8.0256 | 0.9054 | 1.2137 | 9.4303 | 1.103 | 1.2383 | 62.4332 | 1.2281 | 1.2322 | 59.3875 | 1.1735 | 1.2315 | 59.869 | 1.1848 | 324 | 0.90856 | 0.10081 | 1.2142 | 0.016748 | 0.9866 | 0.37356 | 0.65762 | 438.8191 | 1656.3606 | 130.0968 | 384.5861 | 350.4721 | 774.8149 | 582.0592 | 29.0679 | 63.3237 | 47.0804 | 48.4968 | 7.6587 | 0.047247 | 107.1021 | 142.8541 | 40 | 79.7459 | 102.0704 | 131.338 | 40 | 76.7454 | 100.9902 | 76.6033 | 180000.5 | 102.8541 | 0.7521 | 1.646 | 179837 | 0 | 163 | 0.5 | 107.122 | 0.031886 | 0.013 | 178976 | 0.7417 | 1.6808 | 1024.5 | 2.5693 | 102.8541 | 107.9291 | 3.8874 | 163 | 10.9004 | 10.9466 | 11.1733 | 11.3335 | 10.9243 | 109.6485 | 11.2689 | 180003 | 91.338 | 0.16157 | 0.34699 | 180002.5 | 0 | 0 | 0.5 | 102.0716 | 0.031147 | 0.012 | 179233.5 | 0.15984 | 0.3524 | 769.5 | 0.56428 | 91.338 | 103.7702 | 4.8631 | 0 | [7 empty] | 3600 | 61347.3122 | inf | 61347.3122 | 61347.3122 | 5.5024e+23 | 30673.7407 | 102.8541 | 91.4271 | 58579.2766 | inf | 58579.2766 | 58579.2766 | 3.9736e+34 | 29289.6383 | 91.338 | 85.669 | Diode | 7.0031 | 6.6871
Image_B200_ModelSize_512 | B_200 | 3600 | 0.8033 | 1.9175 | 0.42663 | 0.8033 | 2.387 | 1.4566 | 25.1356 | 56.25 | 135 | 1.8117 | 1.8714 | 0.43189 | 1.4395 | 71.9739 | 1.9053 | 13.4976 | 14.16 | 39.9618 | 43.362 | 67 | 53.2579 | 0.11186 | 67.5 | 67.5 | 64.5 | 1.4751 | 0.25389 | 1.4514 | 1.3998 | 0.094154 | 1.2948 | 1.4032 | 1.4794 | 1.4906 | 1.4508 | 0.14291 | 0 | 7.0407 | 85.9347 | 6.7707 | 0.19301 | 0.03806 | 0.022785 | 1.2948 | -0.010248 | 1.0083 | 0.92807 | 0.89534 | 0.84916 | 1.2041 | 1.5488 | 1.6143 | 0.058623 | 0.068953 | 0.070698 | 0.00068792 | 0.00029747 | 0.00029747 | 1.4678 | 11.9198 | 2.4817 | 0.2396 | 1.4715 | 0.31703 | 0.0063997 | 0.013851 | 0.0027702 | 1.4689 | 24.9995 | 2.5707 | 0.4576 | 5.1393 | 0.57563 | 0.022865 | 0.11852 | 0.012069 | 1.459 | 80.6514 | 1.6569 | 1.4565 | 70.2038 | 1.4669 | 1.4558 | 68.1041 | 1.4302 | 132 | 0.96429 | 0.11484 | 1.4476 | 0.052491 | 1.0591 | 0.51671 | 0.77236 | 464.2308 | 1872.5669 | 137.6306 | 434.7865 | 354.4051 | 891.3741 | 697.9813 | 29.2881 | 72.4527 | 56.2056 | 47.9719 | 7.6332 | 0.047764 | 107.7688 | 146.6319 | 40 | 81.6102 | 102.6759 | 133.3076 | 40 | 78.1247 | 101.5879 | 77.7652 | 180000.5 | 106.6319 | 0.76134 | 1.8786 | 179932.5 | 4 | 63.5 | 0.5 | 107.7893 | 0.033368 | 0.013 | 176964.5 | 0.73934 | 1.9526 | 3036 | 2.0439 | 106.6319 | 115.0123 | 1.4537 | 67.5 | 13.1502 | 13.493 | 14.082 | 14.1724 | 13.497 | 110.8896 | 29.5002 | 180000 | 93.3076 | 0.16285 | 0.39376 | 179999.5 | 0 | 0 | 0.5 | 102.6771 | 0.032155 | 0.012 | 179123 | 0.1611 | 0.40686 | 877 | 0.52089 | 93.3076 | 110.8873 | 4.4759 | 0 | [7 empty] | 3600 | 50262.747 | inf | 50262.747 | 50262.747 | 6.3448e+22 | 25132.0972 | 106.6319 | 93.3159 | 52200.4648 | inf | 52200.4648 | 52200.4648 | 4.8129e+33 | 26100.2324 | 93.3076 | 86.6538 | IGBT | 5.7378 | 5.959
Text_B200_BatchSize2 | B_200 | 3600 | 0.8033 | 0.91365 | 0.41787 | 0.8033 | 1.1374 | 0.44722 | 88.8667 | 17.3077 | 208 | 0.64722 | 0.84843 | 0.42714 | 0.42129 | 21.0645 | 0.89686 | 31.2322 | 34 | 3.5638 | 2.7 | 103 | 34.5527 | 0.15805 | 104 | 0 | 0 | 0.48639 | 4.1991e-10 | 0.43384 | 0.20661 | 0.073328 | 0.066628 | 0.41508 | 0.47316 | 0.48682 | 0.42758 | 0.24864 | 0 | 37.3093 | 34.0006 | 27.982 | 0.45967 | 0.20697 | 0.041462 | 0.022982 | 0.0040473 | 0.81233 | 0.83866 | 0.8257 | 0.8258 | 0.36723 | 0.23064 | 0.23479 | 0.039275 | 0.028754 | 0.028861 | 0.020303 | 0.01715 | 0.01715 | 0.45815 | 1.7197 | 0.35178 | 0.11379 | 0.41953 | 0.085327 | 0.045181 | 0.1914 | 0.038285 | 0.45204 | 3.6383 | 0.36816 | 0.17766 | 1.3673 | 0.13876 | 0.053852 | 0.4548 | 0.045488 | 0.43691 | 17.2822 | 0.29022 | 0.30452 | 14.5159 | 0.24451 | 0.33434 | 16.3188 | 0.27394 | 0 | 0.025756 | 0.22988 | 0.26089 | 0.053968 | 0.42737 | 0.088388 | 0.053772 | 373.9903 | 892.239 | 110.877 | 207.1667 | 341.441 | 391.4028 | 197.8929 | 28.5624 | 32.6571 | 16.3383 | 49.7468 | 7.7195 | 0.04606 | 105.4423 | 133.6085 | 40 | 74.3854 | 100.5494 | 127.9134 | 40 | 74.3076 | 99.4875 | 74.0386 | 180000.5 | 93.6085 | 0.73089 | 0.79873 | 180000 | 0 | 0 | 0.5 | 105.4608 | 0.035974 | 0.013 | 177455 | 0.72699 | 0.83365 | 2545.5 | 1.0024 | 93.6085 | 105.9967 | 1.7677 | 0 | [7 empty] | 180000 | 87.9134 | 0.15863 | 0.17291 | 179999.5 | 0 | 0 | 0.5 | 100.5505 | 0.029079 | 0.012 | 178004.5 | 0.15788 | 0.18041 | 1995.5 | 0.22612 | 87.9134 | 106.9085 | 1.5761 | 0 | [7 empty] | 3600 | 102596.4089 | inf | 102596.4089 | 102596.4089 | 5.0535e+28 | 51298.2045 | 93.6085 | 86.8043 | 71950.7822 | inf | 71950.7822 | 71950.7822 | 7.8269e+38 | 35975.3911 | 87.9134 | 83.9567 | Diode | 11.7119 | 8.2136
Text_B200_BatchSize16 | B_200 | 3600 | 0.8033 | 1.0855 | 0.23672 | 0.8033 | 1.3513 | 0.79365 | 75.4422 | 8.4906 | 800 | 1.7844 | 0.99623 | 0.25886 | 0.73736 | 36.8682 | 1.0743 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 400 | 396 | 0 | 0.83718 | 1.6484e-05 | 0.78651 | 0.67937 | 0.15525 | 0.13726 | 0.81477 | 0.83067 | 0.83485 | 0.78521 | 0.6018 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 1.3682e-05 | 0.020177 | 0.8509 | 0.85872 | 0.84852 | 0.84782 | 0.73181 | 0.49566 | 0.5199 | 0.16717 | 0.11456 | 0.11754 | 0.064542 | 0.056811 | 0.057364 | 0.82275 | 3.4618 | 0.72788 | 0.54927 | 2.2012 | 0.46213 | 0.75317 | 2.7678 | 0.58771 | 0.80974 | 7.0507 | 0.73078 | 0.72568 | 6.1097 | 0.63639 | 0.77444 | 6.5815 | 0.68144 | 0.79293 | 40.5526 | 0.7033 | 0.73726 | 37.1055 | 0.6444 | 0.78407 | 39.5943 | 0.6885 | 400 | 0.0572 | 0.59078 | 0.76043 | 0.1196 | 0.85504 | 0.19547 | 0.088606 | 391.7435 | 1060.0526 | 116.1403 | 246.1309 | 343.7709 | 471.7946 | 350.7802 | 28.6928 | 39.1786 | 28.9716 | 49.4182 | 7.7035 | 0.046366 | 106.4106 | 136.6417 | 40 | 75.7643 | 101.4811 | 129.8087 | 40 | 75.5174 | 100.4135 | 75.5253 | 180000.5 | 96.6417 | 0.73636 | 0.96368 | 179604.5 | 395.5 | 0 | 0.5 | 106.4295 | 0.034915 | 0.013 | 177233.5 | 0.72016 | 1.009 | 2767 | 1.7746 | 96.6417 | 106.9768 | 1.6164 | 395.5 | 6.2399 | 6.2304 | 6.4616 | 9.01 | 6.5018 | 104.93 | 4.7097 | 180000 | 89.8087 | 0.15939 | 0.20764 | 179999.5 | 0 | 0 | 0.5 | 101.4822 | 0.032615 | 0.012 | 177337 | 0.1564 | 0.21668 | 2663 | 0.3584 | 89.8087 | 102.4727 | 1.4975 | 0 | [7 empty] | 3600 | 86286.4847 | inf | 86286.4847 | 86286.4847 | 3.6932e+27 | 43143.2425 | 96.6417 | 88.3208 | 64160.9332 | inf | 64160.9332 | 64160.9332 | 7.8777e+37 | 32080.4666 | 89.8087 | 84.9044 | Diode | 9.8501 | 7.3243
Text_B200_BatchSize32 | B_200 | 3600 | 0.8033 | 1.0267 | 0.2189 | 0.8033 | 1.2781 | 0.75138 | 81.3444 | 9.0909 | 808 | 1.8281 | 0.94352 | 0.26962 | 0.6739 | 33.6952 | 1.0176 | 7.2608 | 7.54 | 1.6564 | 1.9 | 403 | 8.9104 | 0.076621 | 408 | 399.5 | 0 | 0.77497 | 7.9339e-06 | 0.69814 | 0.21967 | 0.0079324 | 0.14505 | 0.77085 | 0.79444 | 0.79484 | 0.67928 | 0.024106 | 0 | 0.15471 | 1.1689 | 97.1631 | 0.98678 | 0.44353 | 0.082978 | 0.091847 | 0.00040899 | 0.83679 | 0.82847 | 0.81228 | 0.80873 | 0.66691 | 0.45704 | 0.47735 | 0.19433 | 0.13244 | 0.13575 | 0.15049 | 0.085168 | 0.089256 | 0.77747 | 3.2245 | 0.66894 | 0.55168 | 2.1069 | 0.44279 | 0.72635 | 2.5198 | 0.53973 | 0.77546 | 6.3878 | 0.664 | 0.74498 | 5.9839 | 0.6232 | 0.74669 | 6.0014 | 0.62234 | 0.75973 | 36.9367 | 0.64051 | 0.75184 | 36.2372 | 0.62912 | 0.75217 | 36.2289 | 0.62877 | 396 | 0.075734 | 0.022783 | 0.33609 | 0.0061243 | 0.8386 | 0.25354 | 0.10856 | 385.2493 | 1002.6606 | 114.215 | 232.8052 | 342.9061 | 444.0593 | 330.303 | 28.6444 | 36.9348 | 27.3281 | 49.5397 | 7.7094 | 0.046253 | 105.7249 | 135.0776 | 40 | 75.482 | 100.8093 | 128.4771 | 40 | 74.9778 | 99.7445 | 74.8672 | 180000.5 | 95.0776 | 0.73433 | 0.90768 | 179600.5 | 399.5 | 0 | 0.5 | 105.7436 | 0.036192 | 0.013 | 177512 | 0.71704 | 0.94377 | 2488.5 | 1.9676 | 95.0776 | 106.5391 | 1.8892 | 399.5 | 5.9092 | 5.9176 | 6.1189 | 6.2919 | 5.9301 | 104.5003 | 4.6216 | 180000 | 88.4771 | 0.15911 | 0.19603 | 179999.5 | 0 | 0 | 0.5 | 100.8104 | 0.032314 | 0.012 | 177563.5 | 0.15596 | 0.20397 | 2436.5 | 0.38892 | 88.4771 | 102.4097 | 1.6191 | 0 | [7 empty] | 3600 | 94288.0721 | inf | 94288.0721 | 94288.0721 | 9.6669e+27 | 47144.0361 | 95.0776 | 87.5388 | 69524.4861 | inf | 69524.4861 | 69524.4861 | 1.8377e+38 | 34762.243 | 88.4771 | 84.2385 | Diode | 10.7635 | 7.9366
Text_B200_Deepspeedds_z1 | B_200 | 3600 | 0.8033 | 1.2096 | 0.24646 | 0.8033 | 1.5057 | 0.90666 | 70.1844 | 7.9646 | 824 | 2.2699 | 1.0356 | 0.26656 | 0.76904 | 38.4518 | 1.1995 | 6.1758 | 6.4 | 2.5715 | 2 | 411 | 8.7335 | 0.9838 | 416 | 411.5 | 0 | 0.91054 | 0.00011954 | 0.86108 | 0.71575 | 0.22645 | 0.36434 | 0.92242 | 0.94327 | 0.94869 | 0.84228 | 0.55764 | 0 | 29.0813 | 2.784 | 62.0211 | 5.59 | 0.43961 | 0.08395 | 0.36167 | 0.049411 | 0.86542 | 0.8891 | 0.87346 | 0.86855 | 0.82222 | 0.63164 | 0.65887 | 0.2462 | 0.19345 | 0.19806 | 0.18973 | 0.17384 | 0.17489 | 0.91899 | 4.3295 | 0.89917 | 0.67368 | 2.7973 | 0.59065 | 0.86764 | 3.314 | 0.70897 | 0.91108 | 8.44 | 0.87578 | 0.81308 | 6.9671 | 0.73336 | 0.89175 | 7.6298 | 0.80347 | 0.90241 | 47.3166 | 0.82856 | 0.88304 | 42.9306 | 0.75939 | 0.89524 | 46.2416 | 0.81092 | 421 | 0.27147 | 0.54026 | 0.80431 | 0.17522 | 1.0144 | 0.3856 | 0.18889 | 398.4304 | 1181.2045 | 118.1228 | 274.2608 | 344.6765 | 531.1664 | 404.7848 | 28.7435 | 43.9614 | 33.3239 | 49.2917 | 7.6974 | 0.046485 | 106.7826 | 138.1682 | 40 | 75.6259 | 101.8393 | 130.557 | 40 | 75.4466 | 100.7696 | 75.4675 | 180000.5 | 98.1682 | 0.73849 | 1.062 | 179589 | 409.5 | 1.5 | 0.5 | 106.8016 | 0.034754 | 0.013 | 177906 | 0.71503 | 1.1106 | 2094.5 | 2.7314 | 98.1682 | 106.8961 | 2.1816 | 411 | 7.1868 | 7.1731 | 7.3285 | 11.0291 | 7.6968 | 105.5862 | 4.3902 | 180000 | 90.557 | 0.15969 | 0.22916 | 179999.5 | 0 | 0 | 0.5 | 101.8404 | 0.033343 | 0.012 | 177904.5 | 0.15539 | 0.23909 | 2095.5 | 0.52435 | 90.557 | 101.1949 | 2.0255 | 0 | [7 empty] | 3600 | 79220.6883 | inf | 79220.6883 | 79220.6883 | 1.2822e+27 | 39610.3459 | 98.1682 | 89.0841 | 61358.7327 | inf | 61358.7327 | 61358.7327 | 3.1226e+37 | 30679.3663 | 90.557 | 85.2785 | Diode | 9.0435 | 7.0044
Text_B200_Deepspeedds_z2 | B_200 | 3600 | 0.8033 | 1.1046 | 0.24125 | 0.8033 | 1.3751 | 0.79644 | 74.5778 | 8.5714 | 815 | 1.78 | 1.0034 | 0.25986 | 0.7435 | 37.1752 | 1.0906 | 6.6051 | 6.9 | 2.1171 | 1.94 | 407 | 8.707 | 0.48509 | 407.5 | 396 | 0 | 0.8484 | 2.3169e-05 | 0.78621 | 0.58479 | 0.13165 | 0.5821 | 0.81481 | 0.84577 | 0.84629 | 0.78484 | 0.49169 | 0 | 19.7537 | 2.5003 | 76.5089 | 0.77496 | 0.38857 | 0.073518 | 0.58204 | 0.019315 | 0.85263 | 0.84863 | 0.84549 | 0.84268 | 0.70934 | 0.50169 | 0.51985 | 0.17304 | 0.11846 | 0.12159 | 0.076526 | 0.063197 | 0.06321 | 0.83425 | 3.5443 | 0.74093 | 0.57452 | 2.2747 | 0.47997 | 0.75952 | 2.7527 | 0.58898 | 0.82777 | 7.2246 | 0.74947 | 0.74967 | 6.2391 | 0.65312 | 0.78722 | 6.6268 | 0.69114 | 0.80205 | 40.5956 | 0.70764 | 0.79039 | 38.1299 | 0.66871 | 0.79001 | 39.6418 | 0.69134 | 396 | 0.43414 | 0.48373 | 0.76201 | 0.092023 | 0.87157 | 0.23777 | 0.33102 | 392.5437 | 1078.7098 | 116.3775 | 250.4628 | 343.8785 | 480.8649 | 352.4728 | 28.6988 | 39.9111 | 29.0991 | 49.4032 | 7.7028 | 0.046381 | 106.3301 | 136.5661 | 40 | 75.8455 | 101.399 | 129.6663 | 40 | 75.4925 | 100.3314 | 75.4739 | 180000.5 | 96.5661 | 0.73662 | 0.97319 | 179600.5 | 399.5 | 0 | 0.5 | 106.349 | 0.035042 | 0.013 | 177267.5 | 0.71995 | 1.0289 | 2733 | 1.8176 | 96.5661 | 106.7223 | 1.6372 | 399.5 | 6.319 | 6.3093 | 6.5659 | 8.6213 | 6.4676 | 105.0061 | 4.6765 | 180000 | 89.6663 | 0.15943 | 0.20968 | 179999.5 | 0 | 0 | 0.5 | 101.4001 | 0.033062 | 0.012 | 177371 | 0.15636 | 0.22051 | 2629 | 0.36621 | 89.6663 | 102.1927 | 1.5394 | 0 | [7 empty] | 3600 | 86653.5847 | inf | 86653.5847 | 86653.5847 | 3.1819e+27 | 43326.7924 | 96.5661 | 88.283 | 64710.9594 | inf | 64710.9594 | 64710.9594 | 6.895e+37 | 32355.4797 | 89.6663 | 84.8331 | Diode | 9.892 | 7.3871
Text_B200_Deepspeedds_z3 | B_200 | 3600 | 0.8033 | 1.0855 | 0.23672 | 0.8033 | 1.3513 | 0.79365 | 75.4422 | 8.4906 | 800 | 1.7844 | 0.99623 | 0.25886 | 0.73736 | 36.8682 | 1.0743 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 400 | 396 | 0 | 0.83718 | 1.6484e-05 | 0.78651 | 0.67937 | 0.15525 | 0.13726 | 0.81477 | 0.83067 | 0.83485 | 0.78521 | 0.6018 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 1.3682e-05 | 0.020177 | 0.8509 | 0.85872 | 0.84852 | 0.84782 | 0.73181 | 0.49566 | 0.5199 | 0.16717 | 0.11456 | 0.11754 | 0.064542 | 0.056811 | 0.057364 | 0.82275 | 3.4618 | 0.72788 | 0.54927 | 2.2012 | 0.46213 | 0.75317 | 2.7678 | 0.58771 | 0.80974 | 7.0507 | 0.73078 | 0.72568 | 6.1097 | 0.63639 | 0.77444 | 6.5815 | 0.68144 | 0.79293 | 40.5526 | 0.7033 | 0.73726 | 37.1055 | 0.6444 | 0.78407 | 39.5943 | 0.6885 | 400 | 0.0572 | 0.59078 | 0.76043 | 0.1196 | 0.85504 | 0.19547 | 0.088606 | 391.7435 | 1060.0526 | 116.1403 | 246.1309 | 343.7709 | 471.7946 | 350.7802 | 28.6928 | 39.1786 | 28.9716 | 49.4182 | 7.7035 | 0.046366 | 106.4106 | 136.6417 | 40 | 75.7643 | 101.4811 | 129.8087 | 40 | 75.5174 | 100.4135 | 75.5253 | 180000.5 | 96.6417 | 0.73636 | 0.96368 | 179604.5 | 395.5 | 0 | 0.5 | 106.4295 | 0.034915 | 0.013 | 177233.5 | 0.72016 | 1.009 | 2767 | 1.7746 | 96.6417 | 106.9768 | 1.6164 | 395.5 | 6.2399 | 6.2304 | 6.4616 | 9.01 | 6.5018 | 104.93 | 4.7097 | 180000 | 89.8087 | 0.15939 | 0.20764 | 179999.5 | 0 | 0 | 0.5 | 101.4822 | 0.032615 | 0.012 | 177337 | 0.1564 | 0.21668 | 2663 | 0.3584 | 89.8087 | 102.4727 | 1.4975 | 0 | [7 empty] | 3600 | 86286.4847 | inf | 86286.4847 | 86286.4847 | 3.6932e+27 | 43143.2425 | 96.6417 | 88.3208 | 64160.9332 | inf | 64160.9332 | 64160.9332 | 7.8777e+37 | 32080.4666 | 89.8087 | 84.9044 | Diode | 9.8501 | 7.3243
Text_B200_Lamma_1B | B_200 | 3600 | 0.8033 | 1.2824 | 0.39846 | 0.8033 | 1.5964 | 0.83291 | 48.12 | 4.4776 | 1599 | 2.2717 | 1.1765 | 0.42359 | 0.75287 | 37.6435 | 1.2693 | 2.171 | 2.28 | 2.3326 | 2.522 | 799 | 4.5037 | 0.15552 | 799.5 | 792 | 0 | 0.85865 | 9.7964e-05 | 0.80476 | 0.19419 | 0.016371 | 0.59554 | 0.8335 | 0.87672 | 0.87687 | 0.79917 | 0.063052 | 0 | 0.4565 | 1.1689 | 97.0705 | 0.59672 | 0.59764 | 0.10968 | 0.59554 | -0.0081355 | 0.8643 | 0.82512 | 0.81552 | 0.81001 | 0.74074 | 0.64191 | 0.66278 | 0.32269 | 0.26397 | 0.26913 | 0.31144 | 0.25899 | 0.26451 | 0.86293 | 3.771 | 0.80706 | 0.81822 | 3.3016 | 0.70916 | 0.83017 | 3.3107 | 0.71299 | 0.85437 | 7.3392 | 0.78451 | 0.82941 | 6.6648 | 0.71632 | 0.83046 | 6.6401 | 0.71314 | 0.83842 | 40.8921 | 0.73224 | 0.83216 | 40.109 | 0.71916 | 0.83444 | 40.4247 | 0.72351 | 5 | 0.44798 | 0.058313 | 0.1203 | 0.0064838 | 0.97456 | 0.24228 | 0.33294 | 397.9142 | 1252.3271 | 117.9698 | 290.7746 | 344.606 | 566.5418 | 378.8949 | 28.7395 | 46.7984 | 31.0072 | 49.3015 | 7.6978 | 0.046476 | 106.0344 | 137.4472 | 40 | 76.2947 | 101.0927 | 129.262 | 40 | 75.3571 | 100.0244 | 75.2194 | 180000.5 | 97.4472 | 0.73832 | 1.162 | 179208.5 | 791.5 | 0 | 0.5 | 106.0535 | 0.031659 | 0.013 | 178977 | 0.71011 | 1.2057 | 1023.5 | 5.6717 | 97.4472 | 106.9582 | 3.8952 | 791.5 | 6.9151 | 6.9455 | 7.1514 | 7.3697 | 6.9458 | 106.3885 | 2.7026 | 180000 | 89.262 | 0.15966 | 0.24906 | 179999.5 | 0 | 0 | 0.5 | 101.0939 | 0.030927 | 0.012 | 179020.5 | 0.15464 | 0.25852 | 979.5 | 1.0786 | 89.262 | 102.5691 | 3.8734 | 0 | [7 empty] | 3600 | 82467.6232 | inf | 82467.6232 | 82467.6232 | 2.6931e+26 | 41233.8119 | 97.4472 | 88.7236 | 66301.7614 | inf | 66301.7614 | 66301.7614 | 8.3724e+36 | 33150.8807 | 89.262 | 84.631 | Diode | 9.4141 | 7.5687
Text_B200_Lamma_3B | B_200 | 3600 | 0.8033 | 1.2347 | 0.31466 | 0.8033 | 1.5371 | 0.85785 | 56.9089 | 6.8702 | 1039 | 1.9574 | 1.1399 | 0.32804 | 0.81184 | 40.5919 | 1.219 | 4.2316 | 4.4 | 2.6954 | 2.7 | 519 | 6.9269 | 0.37202 | 520 | 515.5 | 0 | 0.89727 | 0.0001424 | 0.84591 | 0.309 | 0.070296 | 0.44144 | 0.85357 | 0.91638 | 0.9199 | 0.84612 | 0.24077 | 0 | 4.9876 | 1.7824 | 91.691 | 1.0999 | 0.38827 | 0.050956 | 0.42848 | 0.017605 | 0.87368 | 0.84055 | 0.83377 | 0.83101 | 0.75381 | 0.60466 | 0.62585 | 0.22403 | 0.17132 | 0.17507 | 0.21027 | 0.13891 | 0.14291 | 0.8929 | 4.2033 | 0.87203 | 0.80403 | 3.2792 | 0.7066 | 0.84499 | 3.2992 | 0.71532 | 0.88713 | 8.0424 | 0.85199 | 0.8269 | 6.7731 | 0.73084 | 0.85499 | 6.9377 | 0.75266 | 0.86407 | 42.7667 | 0.7692 | 0.85613 | 41.2757 | 0.74687 | 0.85649 | 41.9463 | 0.75713 | 9 | 0.31769 | 0.2304 | 0.49702 | 0.054909 | 1.1237 | 0.17671 | 0.22961 | 402.2354 | 1205.7843 | 119.2509 | 279.9679 | 345.1986 | 543.3485 | 385.9904 | 28.7727 | 44.9394 | 31.6978 | 49.219 | 7.6938 | 0.046554 | 106.2761 | 136.7864 | 40 | 76.2097 | 101.3253 | 128.9645 | 40 | 74.9553 | 100.2556 | 74.9049 | 180000.5 | 96.7864 | 0.73971 | 1.1079 | 179485 | 515 | 0 | 0.5 | 106.2953 | 0.033283 | 0.013 | 178246 | 0.71844 | 1.1765 | 1754.5 | 2.9013 | 96.7864 | 107.969 | 2.4244 | 515 | 7.0513 | 7.0502 | 7.3256 | 8.3433 | 7.0894 | 105.9652 | 4.1418 | 180000 | 88.9645 | 0.15986 | 0.23769 | 179999.5 | 0 | 0 | 0.5 | 101.3264 | 0.031828 | 0.012 | 178302.5 | 0.15604 | 0.25128 | 1697.5 | 0.56072 | 88.9645 | 102.2639 | 2.2983 | 0 | [7 empty] | 3600 | 85583.1774 | inf | 85583.1774 | 85583.1774 | 4.3598e+26 | 42791.589 | 96.7864 | 88.3932 | 67502.4124 | inf | 67502.4124 | 67502.4124 | 1.2174e+37 | 33751.2062 | 88.9645 | 84.4822 | Diode | 9.7698 | 7.7058
Text_B200_Lamma_8B | B_200 | 3600 | 0.8033 | 1.0855 | 0.23672 | 0.8033 | 1.3513 | 0.79365 | 75.4422 | 8.4906 | 800 | 1.7844 | 0.99623 | 0.25886 | 0.73736 | 36.8682 | 1.0743 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 400 | 396 | 0 | 0.83718 | 1.6484e-05 | 0.78651 | 0.67937 | 0.15525 | 0.13726 | 0.81477 | 0.83067 | 0.83485 | 0.78521 | 0.6018 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 1.3682e-05 | 0.020177 | 0.8509 | 0.85872 | 0.84852 | 0.84782 | 0.73181 | 0.49566 | 0.5199 | 0.16717 | 0.11456 | 0.11754 | 0.064542 | 0.056811 | 0.057364 | 0.82275 | 3.4618 | 0.72788 | 0.54927 | 2.2012 | 0.46213 | 0.75317 | 2.7678 | 0.58771 | 0.80974 | 7.0507 | 0.73078 | 0.72568 | 6.1097 | 0.63639 | 0.77444 | 6.5815 | 0.68144 | 0.79293 | 40.5526 | 0.7033 | 0.73726 | 37.1055 | 0.6444 | 0.78407 | 39.5943 | 0.6885 | 400 | 0.0572 | 0.59078 | 0.76043 | 0.1196 | 0.85504 | 0.19547 | 0.088606 | 391.7435 | 1060.0526 | 116.1403 | 246.1309 | 343.7709 | 471.7946 | 350.7802 | 28.6928 | 39.1786 | 28.9716 | 49.4182 | 7.7035 | 0.046366 | 106.4106 | 136.6417 | 40 | 75.7643 | 101.4811 | 129.8087 | 40 | 75.5174 | 100.4135 | 75.5253 | 180000.5 | 96.6417 | 0.73636 | 0.96368 | 179604.5 | 395.5 | 0 | 0.5 | 106.4295 | 0.034915 | 0.013 | 177233.5 | 0.72016 | 1.009 | 2767 | 1.7746 | 96.6417 | 106.9768 | 1.6164 | 395.5 | 6.2399 | 6.2304 | 6.4616 | 9.01 | 6.5018 | 104.93 | 4.7097 | 180000 | 89.8087 | 0.15939 | 0.20764 | 179999.5 | 0 | 0 | 0.5 | 101.4822 | 0.032615 | 0.012 | 177337 | 0.1564 | 0.21668 | 2663 | 0.3584 | 89.8087 | 102.4727 | 1.4975 | 0 | [7 empty] | 3600 | 86286.4847 | inf | 86286.4847 | 86286.4847 | 3.6932e+27 | 43143.2425 | 96.6417 | 88.3208 | 64160.9332 | inf | 64160.9332 | 64160.9332 | 7.8777e+37 | 32080.4666 | 89.8087 | 84.9044 | Diode | 9.8501 | 7.3243
Text_B200_SeqLength_1024 | B_200 | 3600 | 0.8033 | 1.0842 | 0.23792 | 0.8033 | 1.3497 | 0.78762 | 75.46 | 8.7379 | 792 | 1.8029 | 0.99603 | 0.25861 | 0.73742 | 36.8709 | 1.0749 | 6.8683 | 7.03 | 2.1257 | 2.04 | 396 | 8.994 | 0.3737 | 404 | 396 | 0 | 0.8311 | 2.128e-05 | 0.76731 | 0.28897 | 0.10404 | 0.13832 | 0.80828 | 0.83217 | 0.83597 | 0.76322 | 0.37703 | 0 | 15.1867 | 2.5589 | 80.8655 | 0.9394 | 0.38934 | 0.06008 | 0.0043776 | 0.014093 | 0.85044 | 0.8441 | 0.83765 | 0.83416 | 0.73037 | 0.49863 | 0.51978 | 0.17067 | 0.11603 | 0.11907 | 0.073517 | 0.06119 | 0.061565 | 0.81499 | 3.5064 | 0.72776 | 0.57724 | 2.262 | 0.47756 | 0.75581 | 2.6932 | 0.57664 | 0.81149 | 7.1095 | 0.73827 | 0.75416 | 6.2233 | 0.65191 | 0.78181 | 6.5353 | 0.68355 | 0.79386 | 39.6817 | 0.69413 | 0.78506 | 37.8588 | 0.66507 | 0.78584 | 38.9428 | 0.67964 | 404 | 0.059143 | 0.36809 | 0.44012 | 0.073053 | 0.84557 | 0.19207 | 0.091471 | 391.5319 | 1058.7742 | 116.0776 | 245.834 | 343.7425 | 471.174 | 348.3022 | 28.6912 | 39.1285 | 28.762 | 49.4222 | 7.7037 | 0.046363 | 106.2107 | 136.2444 | 40 | 75.8594 | 101.2818 | 129.419 | 40 | 75.4095 | 100.2146 | 75.4286 | 180000.5 | 96.2444 | 0.7363 | 0.96378 | 179604.5 | 395.5 | 0 | 0.5 | 106.2296 | 0.035209 | 0.013 | 177216.5 | 0.71992 | 1.0131 | 2784 | 1.7785 | 96.2444 | 106.8269 | 1.6283 | 395.5 | 6.2836 | 6.2699 | 6.52 | 8.112 | 6.3656 | 104.9385 | 4.7857 | 180000 | 89.419 | 0.15938 | 0.20771 | 179999.5 | 0 | 0 | 0.5 | 101.2829 | 0.03305 | 0.012 | 177283 | 0.15637 | 0.21819 | 2717 | 0.35628 | 89.419 | 102.5158 | 1.4971 | 0 | [7 empty] | 3600 | 88241.1727 | inf | 88241.1727 | 88241.1727 | 3.7368e+27 | 44120.5864 | 96.2444 | 88.1222 | 65679.0901 | inf | 65679.0901 | 65679.0901 | 7.9255e+37 | 32839.545 | 89.419 | 84.7095 | Diode | 10.0732 | 7.4976
Text_B200_SeqLength_2048 | B_200 | 3600 | 0.8033 | 1.0855 | 0.23672 | 0.8033 | 1.3513 | 0.79365 | 75.4422 | 8.4906 | 800 | 1.7844 | 0.99623 | 0.25886 | 0.73736 | 36.8682 | 1.0743 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 400 | 396 | 0 | 0.83718 | 1.6484e-05 | 0.78651 | 0.67937 | 0.15525 | 0.13726 | 0.81477 | 0.83067 | 0.83485 | 0.78521 | 0.6018 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 1.3682e-05 | 0.020177 | 0.8509 | 0.85872 | 0.84852 | 0.84782 | 0.73181 | 0.49566 | 0.5199 | 0.16717 | 0.11456 | 0.11754 | 0.064542 | 0.056811 | 0.057364 | 0.82275 | 3.4618 | 0.72788 | 0.54927 | 2.2012 | 0.46213 | 0.75317 | 2.7678 | 0.58771 | 0.80974 | 7.0507 | 0.73078 | 0.72568 | 6.1097 | 0.63639 | 0.77444 | 6.5815 | 0.68144 | 0.79293 | 40.5526 | 0.7033 | 0.73726 | 37.1055 | 0.6444 | 0.78407 | 39.5943 | 0.6885 | 400 | 0.0572 | 0.59078 | 0.76043 | 0.1196 | 0.85504 | 0.19547 | 0.088606 | 391.7435 | 1060.0526 | 116.1403 | 246.1309 | 343.7709 | 471.7946 | 350.7802 | 28.6928 | 39.1786 | 28.9716 | 49.4182 | 7.7035 | 0.046366 | 106.4106 | 136.6417 | 40 | 75.7643 | 101.4811 | 129.8087 | 40 | 75.5174 | 100.4135 | 75.5253 | 180000.5 | 96.6417 | 0.73636 | 0.96368 | 179604.5 | 395.5 | 0 | 0.5 | 106.4295 | 0.034915 | 0.013 | 177233.5 | 0.72016 | 1.009 | 2767 | 1.7746 | 96.6417 | 106.9768 | 1.6164 | 395.5 | 6.2399 | 6.2304 | 6.4616 | 9.01 | 6.5018 | 104.93 | 4.7097 | 180000 | 89.8087 | 0.15939 | 0.20764 | 179999.5 | 0 | 0 | 0.5 | 101.4822 | 0.032615 | 0.012 | 177337 | 0.1564 | 0.21668 | 2663 | 0.3584 | 89.8087 | 102.4727 | 1.4975 | 0 | [7 empty] | 3600 | 86286.4847 | inf | 86286.4847 | 86286.4847 | 3.6932e+27 | 43143.2425 | 96.6417 | 88.3208 | 64160.9332 | inf | 64160.9332 | 64160.9332 | 7.8777e+37 | 32080.4666 | 89.8087 | 84.9044 | Diode | 9.8501 | 7.3243
Text_B200_SeqLength_4096 | B_200 | 3600 | 0.8033 | 1.0846 | 0.23696 | 0.8033 | 1.3502 | 0.78805 | 75.2956 | 8.6538 | 792 | 1.8167 | 0.99561 | 0.25852 | 0.73709 | 36.8546 | 1.0747 | 6.8543 | 6.985 | 2.1246 | 2.08 | 396 | 8.9789 | 0.43277 | 403.5 | 396 | 0 | 0.82669 | 1.995e-05 | 0.76961 | 0.34214 | 0.1147 | 0.47035 | 0.81082 | 0.82862 | 0.83084 | 0.76628 | 0.42089 | 0 | 17.8616 | 2.5654 | 78.1502 | 0.98671 | 0.36748 | 0.068649 | 0.47035 | 0.020349 | 0.85066 | 0.84505 | 0.83794 | 0.8374 | 0.7035 | 0.49225 | 0.50852 | 0.16921 | 0.11456 | 0.11758 | 0.06737 | 0.05795 | 0.05797 | 0.81629 | 3.4849 | 0.72542 | 0.56095 | 2.2005 | 0.46444 | 0.75635 | 2.7239 | 0.58288 | 0.81026 | 7.0401 | 0.72978 | 0.74817 | 6.1987 | 0.64903 | 0.78197 | 6.5244 | 0.68081 | 0.79352 | 39.8991 | 0.69617 | 0.78513 | 37.8617 | 0.66451 | 0.78538 | 38.9229 | 0.67935 | 400 | 0.34968 | 0.41704 | 0.43599 | 0.077525 | 0.87039 | 0.21923 | 0.29402 | 391.6364 | 1059.1816 | 116.1086 | 245.9286 | 343.7565 | 471.3718 | 348.4775 | 28.692 | 39.1445 | 28.7768 | 49.4202 | 7.7036 | 0.046365 | 106.2538 | 136.3974 | 40 | 75.8472 | 101.3246 | 129.537 | 40 | 75.4456 | 100.2574 | 75.4023 | 180000.5 | 96.3974 | 0.73633 | 0.96388 | 179604.5 | 395.5 | 0 | 0.5 | 106.2727 | 0.034957 | 0.013 | 177231.5 | 0.72004 | 1.0016 | 2769 | 1.7793 | 96.3974 | 107.1509 | 1.6201 | 395.5 | 6.2723 | 6.2532 | 6.5007 | 8.3645 | 6.3794 | 104.937 | 4.7193 | 180000 | 89.537 | 0.15939 | 0.2077 | 179999.5 | 0 | 0 | 0.5 | 101.3257 | 0.032705 | 0.012 | 177319 | 0.15639 | 0.21558 | 2681 | 0.35774 | 89.537 | 102.5533 | 1.4929 | 0 | [7 empty] | 3600 | 87482.6882 | inf | 87482.6882 | 87482.6882 | 3.7281e+27 | 43741.3441 | 96.3974 | 88.1987 | 65214.8882 | inf | 65214.8882 | 65214.8882 | 7.9211e+37 | 32607.4441 | 89.537 | 84.7685 | Diode | 9.9866 | 7.4446

## Load_characteristics
scenario | chip | duration_s | P_mean_MW | P_max_MW | P_min_MW | Energy_MWh | Peak_to_mean | Swing_p95_p05_MW | Time_at_high_load_pct | Dominant_period_s | Transitions_per_h | Ramp_p99_MW_per_s | P_high_level_MW | P_low_level_MW | Step_height_MW | Step_height_pct_rating | P_p999_MW | Dwell_high_mean_s | Dwell_high_p95_s | Dwell_low_mean_s | Dwell_low_p95_s | Bursts_per_h | Burst_period_mean_s | Burst_period_CV | Power_cycles_ge_10pct_per_h | Power_cycles_ge_30pct_per_h | Power_cycles_ge_50pct_per_h | Power_cycle_dP_max_MW | Damage_proxy_per_h | Swing_filtered_tau0.26s_MW | Swing_filtered_tau3.31s_MW | Swing_filtered_tau159s_MW | Max_change_in_0.1s_MW | Max_change_in_1s_MW | Max_change_in_5s_MW | Max_change_in_60s_MW | Swing_avg_1s_MW | Swing_avg_60s_MW | Swing_avg_900s_MW | Var_share_0_0.017Hz_pct | Var_share_0.017_0.1Hz_pct | Var_share_0.1_0.5Hz_pct | Var_share_0.5_0.8Hz_pct | Var_share_0.8_2Hz_pct | Var_share_2_25Hz_pct | Seam_jump_max_MW | Startup_60s_mean_minus_block_mean_MW | P_rms_MW | P_max_avg_60s_MW | P_max_avg_180s_MW | P_max_avg_300s_MW | Swing_period1s_max_MW | Swing_period1s_max_MW_x_E_MJ | Swing_period1s_max_MW_x_Prms_MW | Swing_period1s_mean_MW | Swing_period1s_mean_MW_x_E_MJ | Swing_period1s_mean_MW_x_Prms_MW | Swing_period1s_median_MW | Swing_period1s_median_MW_x_E_MJ | Swing_period1s_median_MW_x_Prms_MW | Swing_period5s_max_MW | Swing_period5s_max_MW_x_E_MJ | Swing_period5s_max_MW_x_Prms_MW | Swing_period5s_mean_MW | Swing_period5s_mean_MW_x_E_MJ | Swing_period5s_mean_MW_x_Prms_MW | Swing_period5s_median_MW | Swing_period5s_median_MW_x_E_MJ | Swing_period5s_median_MW_x_Prms_MW | Swing_period10s_max_MW | Swing_period10s_max_MW_x_E_MJ | Swing_period10s_max_MW_x_Prms_MW | Swing_period10s_mean_MW | Swing_period10s_mean_MW_x_E_MJ | Swing_period10s_mean_MW_x_Prms_MW | Swing_period10s_median_MW | Swing_period10s_median_MW_x_E_MJ | Swing_period10s_median_MW_x_Prms_MW | Swing_period60s_max_MW | Swing_period60s_max_MW_x_E_MJ | Swing_period60s_max_MW_x_Prms_MW | Swing_period60s_mean_MW | Swing_period60s_mean_MW_x_E_MJ | Swing_period60s_mean_MW_x_Prms_MW | Swing_period60s_median_MW | Swing_period60s_median_MW_x_E_MJ | Swing_period60s_median_MW_x_Prms_MW | ERCOT_changes_gt25pct_in_5s_per_h | LIPA_band_5_23.75Hz_amp_10s_MW | Ramp_max_MW_per_min | Swing_avg_4s_MW | Swing_avg_300s_MW | SoCo_band_0.1_0.5Hz_amp_60s_MW | SoCo_band_0.5_0.8Hz_amp_60s_MW | SoCo_band_0.8_2Hz_amp_60s_MW
Image_H100_BatchSize_128 | H_100 | 3600 | 0.8033 | 1.5502 | 0.45403 | 0.8033 | 1.9298 | 1.0506 | 33.7089 | 16.0714 | 464 | 2.0633 | 1.4693 | 0.45833 | 1.011 | 50.5479 | 1.5444 | 5.208 | 5.52 | 10.2948 | 11.213 | 231 | 15.5036 | 0.14852 | 236.5 | 228 | 224 | 1.091 | 0.0024742 | 1.0478 | 0.72913 | 0.026758 | 0.30343 | 1.0322 | 1.0942 | 1.0943 | 1.0462 | 0.070776 | 0 | 0.14094 | 76.0438 | 23.3736 | 0.37502 | 0.053716 | 0.012963 | 0.3003 | 0.014918 | 0.92258 | 0.87543 | 0.837 | 0.81596 | 0.91442 | 0.94195 | 0.97698 | 0.12199 | 0.11995 | 0.1229 | 0.0095594 | 0.010055 | 0.010056 | 1.0767 | 7.0481 | 1.4694 | 0.5724 | 2.7618 | 0.59487 | 0.70023 | 2.8426 | 0.63149 | 1.0905 | 10.8153 | 1.2 | 0.91971 | 7.7772 | 0.87336 | 1.0336 | 8.7007 | 0.99532 | 1.0792 | 52.7207 | 1.006 | 1.0475 | 50.4945 | 0.9662 | 1.0454 | 51.1449 | 0.97369 | 440 | 0.23034 | 0.067919 | 0.99221 | 0.0022511 | 0.99818 | 0.18473 | 0.14759
Image_H100_BatchSize_256 | H_100 | 3600 | 0.8033 | 1.215 | 0.47097 | 0.8033 | 1.5125 | 0.72885 | 45.1533 | 18 | 399 | 1.3796 | 1.1947 | 0.4786 | 0.71615 | 35.8074 | 1.2121 | 8.1003 | 8.38 | 9.9176 | 10.52 | 199 | 18.0179 | 0.10673 | 199.5 | 199.5 | 0 | 0.74075 | 3.3897e-06 | 0.72782 | 0.59262 | 0.023894 | 0.71897 | 0.72337 | 0.73686 | 0.7421 | 0.72735 | 0.071874 | 0 | 0.12143 | 86.4639 | 12.9889 | 0.36003 | 0.042305 | 0.023434 | 0.71761 | -0.02658 | 0.87233 | 0.85432 | 0.81402 | 0.81916 | 0.60947 | 0.53264 | 0.54231 | 0.074024 | 0.063323 | 0.064246 | 0.0092519 | 0.0097972 | 0.0097979 | 0.73273 | 3.9051 | 0.80065 | 0.35149 | 1.4693 | 0.3085 | 0.34688 | 1.2743 | 0.26459 | 0.73369 | 7.6411 | 0.78981 | 0.6823 | 5.5871 | 0.59503 | 0.72248 | 5.7901 | 0.6286 | 0.73274 | 37.2011 | 0.66871 | 0.7284 | 35.1088 | 0.63521 | 0.72897 | 34.7271 | 0.62886 | 391 | 0.53561 | 0.069558 | 0.72236 | 0.012842 | 0.86458 | 0.21262 | 0.38585
Image_H100_BatchSize_512 | H_100 | 3600 | 0.8033 | 2 | 0.44914 | 0.8033 | 2.4897 | 1.5114 | 16.4356 | 14.0625 | 312 | 2.7442 | 1.957 | 0.45874 | 1.4983 | 74.9132 | 1.9953 | 3.32 | 3.34 | 17.5289 | 11 | 156 | 20.849 | 2.3419 | 243.5 | 239.5 | 156 | 1.536 | 1.2387 | 1.5038 | 0.78566 | 0.05031 | 1.1307 | 1.4284 | 1.5448 | 1.5501 | 1.5043 | 0.13957 | 0 | 0.24609 | 64.7699 | 34.2835 | 0.57758 | 0.078517 | 0.044399 | 0.74057 | -0.041514 | 0.94937 | 0.88623 | 0.83791 | 0.83372 | 1.3213 | 1.7435 | 1.8199 | 0.15689 | 0.17984 | 0.18535 | 0.03074 | 0.020103 | 0.02011 | 1.5339 | 11.1031 | 2.396 | 0.67256 | 3.4644 | 0.77473 | 0.64419 | 2.128 | 0.45074 | 1.5349 | 14.8428 | 1.7807 | 1.0807 | 9.1657 | 1.0756 | 1.0587 | 7.4928 | 0.78094 | 1.5297 | 79.6149 | 1.6263 | 1.2143 | 59.1898 | 1.18 | 1.5175 | 72.6247 | 1.4934 | 317 | 0.84326 | 0.13957 | 1.1025 | 0.050727 | 1.3685 | 0.32576 | 0.60436
Image_H100_ImageSize_16 | H_100 | 3600 | 0.8033 | 1.3142 | 0.56126 | 0.8033 | 1.636 | 0.72392 | 32.7044 | 12 | 599 | 1.3695 | 1.2729 | 0.5728 | 0.70012 | 35.0061 | 1.3077 | 3.9323 | 4.16 | 8.0807 | 8.68 | 299 | 12.013 | 0.040278 | 303.5 | 292 | 0 | 0.74665 | 4.3387e-06 | 0.72045 | 0.41438 | 0.014743 | 0.65282 | 0.70996 | 0.74229 | 0.74469 | 0.7183 | 0.020573 | 0 | 0.12879 | 76.108 | 22.97 | 0.67663 | 0.093389 | 0.023176 | 0.59326 | -0.0030773 | 0.85991 | 0.81309 | 0.80765 | 0.80715 | 0.63301 | 0.60936 | 0.62275 | 0.10935 | 0.10247 | 0.10398 | 0.0066616 | 0.0046484 | 0.0046485 | 0.73419 | 4.0901 | 0.83842 | 0.49919 | 2.2329 | 0.46738 | 0.69876 | 2.8135 | 0.59701 | 0.7353 | 6.2814 | 0.67213 | 0.71599 | 5.753 | 0.61426 | 0.71796 | 5.9985 | 0.64072 | 0.73043 | 35.2601 | 0.62909 | 0.72275 | 34.835 | 0.62149 | 0.72302 | 34.8648 | 0.62167 | 304 | 0.43691 | 0.015417 | 0.61505 | 0.0062398 | 0.60965 | 0.26273 | 0.39163
Image_H100_ImageSize_32 | H_100 | 3600 | 0.8033 | 1.5502 | 0.45403 | 0.8033 | 1.9298 | 1.0506 | 33.7089 | 16.0714 | 464 | 2.0633 | 1.4693 | 0.45833 | 1.011 | 50.5479 | 1.5444 | 5.208 | 5.52 | 10.2948 | 11.213 | 231 | 15.5036 | 0.14852 | 236.5 | 228 | 224 | 1.091 | 0.0024742 | 1.0478 | 0.72913 | 0.026758 | 0.30343 | 1.0322 | 1.0942 | 1.0943 | 1.0462 | 0.070776 | 0 | 0.14094 | 76.0438 | 23.3736 | 0.37502 | 0.053716 | 0.012963 | 0.3003 | 0.014918 | 0.92258 | 0.87543 | 0.837 | 0.81596 | 0.91442 | 0.94195 | 0.97698 | 0.12199 | 0.11995 | 0.1229 | 0.0095594 | 0.010055 | 0.010056 | 1.0767 | 7.0481 | 1.4694 | 0.5724 | 2.7618 | 0.59487 | 0.70023 | 2.8426 | 0.63149 | 1.0905 | 10.8153 | 1.2 | 0.91971 | 7.7772 | 0.87336 | 1.0336 | 8.7007 | 0.99532 | 1.0792 | 52.7207 | 1.006 | 1.0475 | 50.4945 | 0.9662 | 1.0454 | 51.1449 | 0.97369 | 440 | 0.23034 | 0.067919 | 0.99221 | 0.0022511 | 0.99818 | 0.18473 | 0.14759
Image_H100_ImageSize_64 | H_100 | 3600 | 0.8033 | 1.1303 | 0.24342 | 0.8033 | 1.407 | 0.87041 | 64.3933 | 21.9512 | 351 | 1.5682 | 1.1031 | 0.25235 | 0.85077 | 42.5386 | 1.1275 | 13.2267 | 14.14 | 7.3102 | 8.24 | 175 | 20.5369 | 0.18647 | 179.5 | 175.5 | 0 | 0.88011 | 5.9861e-05 | 0.8687 | 0.71098 | 0.026278 | 0.83326 | 0.83858 | 0.87673 | 0.88215 | 0.86832 | 0.0895 | 0 | 0.1568 | 89.7647 | 9.6777 | 0.31453 | 0.054986 | 0.031336 | 0.83311 | 0.040884 | 0.89208 | 0.86315 | 0.81949 | 0.82028 | 0.75095 | 0.55262 | 0.57925 | 0.082163 | 0.059085 | 0.060779 | 0.014711 | 0.015583 | 0.015583 | 0.87079 | 4.2152 | 0.87422 | 0.37603 | 1.2924 | 0.28478 | 0.15284 | 0.47831 | 0.1014 | 0.87353 | 8.7052 | 0.89236 | 0.66091 | 4.7288 | 0.53074 | 0.85572 | 5.0579 | 0.61348 | 0.87177 | 43.9909 | 0.80225 | 0.86589 | 41.7346 | 0.77221 | 0.86513 | 41.3086 | 0.76925 | 329 | 0.6215 | 0.0895 | 0.86362 | 0.017481 | 1.2162 | 0.22807 | 0.45725
Image_H100_ModelSize_128 | H_100 | 3600 | 0.8033 | 1.5502 | 0.45403 | 0.8033 | 1.9298 | 1.0506 | 33.7089 | 16.0714 | 464 | 2.0633 | 1.4693 | 0.45833 | 1.011 | 50.5479 | 1.5444 | 5.208 | 5.52 | 10.2948 | 11.213 | 231 | 15.5036 | 0.14852 | 236.5 | 228 | 224 | 1.091 | 0.0024742 | 1.0478 | 0.72913 | 0.026758 | 0.30343 | 1.0322 | 1.0942 | 1.0943 | 1.0462 | 0.070776 | 0 | 0.14094 | 76.0438 | 23.3736 | 0.37502 | 0.053716 | 0.012963 | 0.3003 | 0.014918 | 0.92258 | 0.87543 | 0.837 | 0.81596 | 0.91442 | 0.94195 | 0.97698 | 0.12199 | 0.11995 | 0.1229 | 0.0095594 | 0.010055 | 0.010056 | 1.0767 | 7.0481 | 1.4694 | 0.5724 | 2.7618 | 0.59487 | 0.70023 | 2.8426 | 0.63149 | 1.0905 | 10.8153 | 1.2 | 0.91971 | 7.7772 | 0.87336 | 1.0336 | 8.7007 | 0.99532 | 1.0792 | 52.7207 | 1.006 | 1.0475 | 50.4945 | 0.9662 | 1.0454 | 51.1449 | 0.97369 | 440 | 0.23034 | 0.067919 | 0.99221 | 0.0022511 | 0.99818 | 0.18473 | 0.14759
Image_H100_ModelSize_256 | H_100 | 3600 | 0.8033 | 1.6911 | 0.37693 | 0.8033 | 2.1051 | 1.29 | 32.9644 | 28.125 | 255 | 2.3071 | 1.6545 | 0.38255 | 1.272 | 63.5989 | 1.6841 | 9.2846 | 9.56 | 18.8965 | 20.58 | 127 | 28.1811 | 0.044136 | 127.5 | 127.5 | 127.5 | 1.3018 | 0.057515 | 1.2883 | 1.151 | 0.04492 | 1.2868 | 1.2875 | 1.3057 | 1.3126 | 1.2879 | 0.07961 | 0 | 0.066424 | 90.502 | 9.0844 | 0.27694 | 0.047383 | 0.022924 | 1.2831 | -0.024543 | 0.98893 | 0.91294 | 0.84791 | 0.82151 | 1.1209 | 1.2421 | 1.3032 | 0.085755 | 0.089498 | 0.092511 | 0.0015863 | 0.00061013 | 0.00061013 | 1.2948 | 9.2715 | 1.926 | 0.41181 | 2.0655 | 0.45684 | 0.036101 | 0.21493 | 0.042987 | 1.2958 | 19.4712 | 1.9986 | 0.81092 | 8.2571 | 0.92378 | 1.2275 | 8.5584 | 1.0688 | 1.2951 | 66.5582 | 1.3505 | 1.2898 | 62.1688 | 1.275 | 1.2889 | 60.4972 | 1.2472 | 255 | 0.95754 | 0.07961 | 1.2822 | 0.010771 | 1.0031 | 0.39342 | 0.69028
Image_H100_ModelSize_512 | H_100 | 3600 | 0.8033 | 1.9424 | 0.36713 | 0.8033 | 2.418 | 1.5181 | 28.5533 | 81.8182 | 88 | 1.5689 | 1.8708 | 0.37249 | 1.4983 | 74.9168 | 1.9024 | 23.3395 | 25.594 | 58.4218 | 61.84 | 43 | 81.535 | 0.029494 | 48 | 44 | 44 | 1.5265 | 0.35232 | 1.5131 | 1.5034 | 0.14126 | 0.23905 | 1.419 | 1.5231 | 1.575 | 1.5125 | 0.54476 | 0 | 62.8663 | 32.8057 | 4.2261 | 0.080502 | 0.012778 | 0.00858 | 0.016577 | -0.097917 | 1.0441 | 1.0222 | 0.94044 | 0.85185 | 1.2595 | 1.5656 | 1.6494 | 0.044336 | 0.053387 | 0.05502 | 0.00048787 | 0.00018417 | 0.00018417 | 1.5125 | 11.8046 | 2.4399 | 0.18457 | 0.96799 | 0.21964 | 0.0028052 | 0.0053152 | 0.001063 | 1.5149 | 23.4085 | 2.5005 | 0.35662 | 4.1342 | 0.46937 | 0.0077248 | 0.029367 | 0.0029368 | 1.5228 | 87.239 | 1.8179 | 1.4219 | 70.8071 | 1.5037 | 1.5187 | 83.8167 | 1.7697 | 88 | 0.17775 | 0.5391 | 1.5103 | 0.052448 | 1.0782 | 0.19097 | 0.14716
Text_H100_BatchSize2 | H_100 | 3600 | 0.8033 | 0.94546 | 0.3642 | 0.8033 | 1.177 | 0.5202 | 88.9067 | 45 | 176 | 0.67003 | 0.85367 | 0.37468 | 0.47899 | 23.9496 | 0.93544 | 36.5216 | 43.42 | 4.2636 | 4.82 | 87 | 40.6368 | 0.30187 | 84 | 0 | 0 | 0.56681 | 5.8488e-09 | 0.50713 | 0.30785 | 0.099195 | 0.073195 | 0.46733 | 0.56431 | 0.57069 | 0.4998 | 0.34725 | 0 | 44.0966 | 33.5729 | 21.1307 | 0.99992 | 0.13405 | 0.065896 | 0.016875 | 0.024779 | 0.81517 | 0.84355 | 0.83315 | 0.83452 | 0.41288 | 0.265 | 0.26972 | 0.050243 | 0.037891 | 0.038036 | 0.032146 | 0.027208 | 0.027209 | 0.5281 | 2.0437 | 0.41835 | 0.1412 | 0.53098 | 0.10802 | 0.073059 | 0.30832 | 0.06168 | 0.52792 | 4.0017 | 0.4086 | 0.19521 | 1.4897 | 0.15154 | 0.084669 | 0.71982 | 0.072012 | 0.50114 | 21.4749 | 0.36187 | 0.32064 | 15.1735 | 0.25604 | 0.26262 | 13.1928 | 0.2212 | 116 | 0.059827 | 0.33177 | 0.33683 | 0.078585 | 0.48375 | 0.14127 | 0.061885
Text_H100_BatchSize16 | H_100 | 3600 | 0.8033 | 1.018 | 0.18971 | 0.8033 | 1.2673 | 0.77198 | 85.6422 | 13.4328 | 536 | 1.7048 | 0.91924 | 0.20611 | 0.71313 | 35.6564 | 1.0069 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 352 | 268 | 0 | 0.80419 | 1.2171e-05 | 0.7229 | 0.28569 | 0.0092759 | 0.12383 | 0.78922 | 0.82273 | 0.82536 | 0.70356 | 0.037152 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.081189 | 0.009089 | 0.83422 | 0.82427 | 0.81209 | 0.80857 | 0.68357 | 0.44018 | 0.46108 | 0.15539 | 0.10397 | 0.10652 | 0.062593 | 0.052909 | 0.053101 | 0.79943 | 3.3657 | 0.70053 | 0.43584 | 1.5818 | 0.33461 | 0.34234 | 1.49 | 0.30116 | 0.80769 | 6.6649 | 0.68652 | 0.66948 | 5.2965 | 0.55209 | 0.76206 | 5.8457 | 0.61561 | 0.78168 | 38.131 | 0.65897 | 0.7705 | 37.1378 | 0.64273 | 0.77098 | 37.3601 | 0.64354 | 268 | 0.065105 | 0.037152 | 0.39111 | 0.006674 | 0.80098 | 0.21051 | 0.11513
Text_H100_BatchSize32 | H_100 | 3600 | 0.8033 | 0.99716 | 0.18458 | 0.8033 | 1.2413 | 0.76581 | 87.36 | 14.2857 | 503 | 1.7563 | 0.90302 | 0.20048 | 0.70254 | 35.1268 | 0.98553 | 12.5153 | 12.84 | 1.7927 | 1.96 | 251 | 14.308 | 0.045065 | 404 | 251.5 | 0 | 0.78744 | 1.018e-05 | 0.70032 | 0.26146 | 0.007016 | 0.50398 | 0.78255 | 0.8111 | 0.81257 | 0.67223 | 0.025405 | 0 | 0.062454 | 35.0869 | 62.2372 | 1.967 | 0.54333 | 0.10309 | 0.42999 | -0.0077049 | 0.83091 | 0.82068 | 0.81048 | 0.80754 | 0.69131 | 0.4214 | 0.44438 | 0.15417 | 0.10447 | 0.10693 | 0.071695 | 0.060898 | 0.060918 | 0.78995 | 3.1248 | 0.64686 | 0.42335 | 1.5595 | 0.32864 | 0.30314 | 1.3169 | 0.26501 | 0.78138 | 6.4466 | 0.66303 | 0.63134 | 4.9742 | 0.51712 | 0.75389 | 5.7205 | 0.59988 | 0.77112 | 37.6462 | 0.64786 | 0.76184 | 36.7188 | 0.63301 | 0.76186 | 36.6418 | 0.63218 | 252 | 0.31817 | 0.01923 | 0.34266 | 0.0012444 | 0.87443 | 0.17972 | 0.23839
Text_H100_Deepspeedds_z1 | H_100 | 3600 | 0.8033 | 1.1511 | 0.1985 | 0.8033 | 1.433 | 0.92198 | 73.1756 | 13.0435 | 1104 | 2.1884 | 1.0066 | 0.22305 | 0.7836 | 39.1798 | 1.1419 | 4.7976 | 8.81 | 1.7197 | 2.96 | 551 | 6.5102 | 0.43421 | 1248.5 | 276 | 0 | 0.92534 | 0.00022912 | 0.89344 | 0.38189 | 0.021539 | 0.24586 | 0.92514 | 0.94487 | 0.94487 | 0.88629 | 0.0565 | 0 | 0.15517 | 45.5815 | 51.7663 | 1.9907 | 0.44603 | 0.060206 | 0.21442 | -0.0094018 | 0.85978 | 0.83983 | 0.81721 | 0.81782 | 0.83996 | 0.61033 | 0.64511 | 0.3098 | 0.24703 | 0.25254 | 0.28736 | 0.24665 | 0.24853 | 0.92755 | 4.0988 | 0.85765 | 0.68413 | 2.5981 | 0.55785 | 0.74413 | 2.7018 | 0.57651 | 0.92782 | 8.2685 | 0.85956 | 0.86226 | 6.8628 | 0.73575 | 0.92058 | 6.9766 | 0.75765 | 0.9246 | 46.0134 | 0.81283 | 0.92198 | 44.4379 | 0.79262 | 0.92195 | 44.455 | 0.79286 | 268 | 0.15753 | 0.0352 | 0.5321 | 0.013313 | 0.94231 | 0.36689 | 0.14954
Text_H100_Deepspeedds_z2 | H_100 | 3600 | 0.8033 | 1.0446 | 0.19433 | 0.8033 | 1.3003 | 0.78107 | 84.7 | 13.4328 | 559 | 1.5899 | 0.92662 | 0.21031 | 0.71631 | 35.8156 | 1.0262 | 10.9229 | 11.56 | 1.9639 | 2.14 | 279 | 12.8576 | 0.14207 | 419.5 | 275.5 | 0 | 0.82427 | 1.6049e-05 | 0.73555 | 0.29734 | 0.012159 | 0.73569 | 0.80382 | 0.84405 | 0.84412 | 0.72974 | 0.041142 | 0 | 0.3005 | 45.118 | 51.8542 | 2.128 | 0.42275 | 0.17648 | 0.71233 | -0.0082566 | 0.83616 | 0.82598 | 0.81338 | 0.81083 | 0.72175 | 0.45335 | 0.48291 | 0.16783 | 0.11472 | 0.11747 | 0.073916 | 0.062622 | 0.062735 | 0.81304 | 3.3864 | 0.70308 | 0.45058 | 1.638 | 0.34682 | 0.39787 | 1.7305 | 0.35025 | 0.81561 | 6.8252 | 0.7068 | 0.69913 | 5.554 | 0.57929 | 0.76653 | 5.926 | 0.6211 | 0.79071 | 38.7552 | 0.66931 | 0.78068 | 37.6263 | 0.65271 | 0.7805 | 37.5452 | 0.65451 | 273 | 0.52831 | 0.027611 | 0.40874 | 0.0030646 | 0.94675 | 0.22385 | 0.39202
Text_H100_Deepspeedds_z3 | H_100 | 3600 | 0.8033 | 1.018 | 0.18971 | 0.8033 | 1.2673 | 0.77198 | 85.6422 | 13.4328 | 536 | 1.7048 | 0.91924 | 0.20611 | 0.71313 | 35.6564 | 1.0069 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 352 | 268 | 0 | 0.80419 | 1.2171e-05 | 0.7229 | 0.28569 | 0.0092759 | 0.12383 | 0.78922 | 0.82273 | 0.82536 | 0.70356 | 0.037152 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.081189 | 0.009089 | 0.83422 | 0.82427 | 0.81209 | 0.80857 | 0.68357 | 0.44018 | 0.46108 | 0.15539 | 0.10397 | 0.10652 | 0.062593 | 0.052909 | 0.053101 | 0.79943 | 3.3657 | 0.70053 | 0.43584 | 1.5818 | 0.33461 | 0.34234 | 1.49 | 0.30116 | 0.80769 | 6.6649 | 0.68652 | 0.66948 | 5.2965 | 0.55209 | 0.76206 | 5.8457 | 0.61561 | 0.78168 | 38.131 | 0.65897 | 0.7705 | 37.1378 | 0.64273 | 0.77098 | 37.3601 | 0.64354 | 268 | 0.065105 | 0.037152 | 0.39111 | 0.006674 | 0.80098 | 0.21051 | 0.11513
Text_H100_Lamma_1B | H_100 | 3600 | 0.8033 | 1.363 | 0.29308 | 0.8033 | 1.6967 | 1.0028 | 50.7711 | 4.9451 | 1423 | 2.4306 | 1.2554 | 0.34118 | 0.91426 | 45.713 | 1.341 | 2.5587 | 2.65 | 2.4997 | 2.58 | 711 | 5.0585 | 0.19477 | 716 | 711.5 | 120 | 1.0308 | 0.0025411 | 0.97753 | 0.25672 | 0.037371 | 0.55691 | 1.0177 | 1.0618 | 1.063 | 0.98388 | 0.11051 | 0 | 1.1207 | 1.447 | 95.5842 | 0.887 | 0.89019 | 0.0709 | 0.55691 | 0.0078411 | 0.8899 | 0.83294 | 0.82412 | 0.81979 | 0.907 | 0.77441 | 0.81957 | 0.35131 | 0.28246 | 0.2907 | 0.34527 | 0.26293 | 0.26956 | 1.0432 | 4.3238 | 0.95466 | 0.98434 | 3.9828 | 0.88032 | 0.99727 | 4.0471 | 0.89585 | 1.0317 | 8.6511 | 0.9518 | 0.98856 | 7.998 | 0.88399 | 0.99984 | 8.1218 | 0.8983 | 1.0094 | 49.4873 | 0.91115 | 1.0026 | 48.3253 | 0.892 | 1.002 | 48.8175 | 0.89749 | 5 | 0.41701 | 0.095943 | 0.25732 | 0.025958 | 1.1806 | 0.30359 | 0.34203
Text_H100_Lamma_3B | H_100 | 3600 | 0.8033 | 1.1542 | 0.22271 | 0.8033 | 1.4368 | 0.86997 | 72.2444 | 8.2569 | 856 | 1.9553 | 1.0578 | 0.23324 | 0.82456 | 41.2281 | 1.1347 | 6.0707 | 6.26 | 2.345 | 2.36 | 427 | 8.4043 | 0.20018 | 428 | 427.5 | 0 | 0.90821 | 0.00015446 | 0.85675 | 0.32197 | 0.054197 | 0.29943 | 0.87656 | 0.92285 | 0.92296 | 0.85914 | 0.18832 | 0 | 3.4802 | 3.5882 | 90.8855 | 1.6989 | 0.29457 | 0.052616 | 0.29826 | 0.00069069 | 0.86547 | 0.84165 | 0.82368 | 0.82435 | 0.76455 | 0.55552 | 0.5777 | 0.19763 | 0.13655 | 0.14064 | 0.09049 | 0.069116 | 0.069318 | 0.90299 | 4.2365 | 0.87887 | 0.72406 | 2.8271 | 0.60745 | 0.84762 | 2.908 | 0.64416 | 0.8947 | 7.7614 | 0.8243 | 0.85543 | 6.9338 | 0.74265 | 0.86644 | 7.1447 | 0.7584 | 0.87751 | 43.5655 | 0.77258 | 0.86944 | 41.9074 | 0.75199 | 0.87131 | 42.4168 | 0.75762 | 429 | 0.22252 | 0.16161 | 0.52293 | 0.03895 | 1.0403 | 0.24441 | 0.18343
Text_H100_Lamma_8B | H_100 | 3600 | 0.8033 | 1.018 | 0.18971 | 0.8033 | 1.2673 | 0.77198 | 85.6422 | 13.4328 | 536 | 1.7048 | 0.91924 | 0.20611 | 0.71313 | 35.6564 | 1.0069 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 352 | 268 | 0 | 0.80419 | 1.2171e-05 | 0.7229 | 0.28569 | 0.0092759 | 0.12383 | 0.78922 | 0.82273 | 0.82536 | 0.70356 | 0.037152 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.081189 | 0.009089 | 0.83422 | 0.82427 | 0.81209 | 0.80857 | 0.68357 | 0.44018 | 0.46108 | 0.15539 | 0.10397 | 0.10652 | 0.062593 | 0.052909 | 0.053101 | 0.79943 | 3.3657 | 0.70053 | 0.43584 | 1.5818 | 0.33461 | 0.34234 | 1.49 | 0.30116 | 0.80769 | 6.6649 | 0.68652 | 0.66948 | 5.2965 | 0.55209 | 0.76206 | 5.8457 | 0.61561 | 0.78168 | 38.131 | 0.65897 | 0.7705 | 37.1378 | 0.64273 | 0.77098 | 37.3601 | 0.64354 | 268 | 0.065105 | 0.037152 | 0.39111 | 0.006674 | 0.80098 | 0.21051 | 0.11513
Text_H100_SeqLength_1024 | H_100 | 3600 | 0.8033 | 1.0231 | 0.18862 | 0.8033 | 1.2736 | 0.77154 | 85.7133 | 6.6667 | 544 | 1.5805 | 0.91929 | 0.21004 | 0.70925 | 35.4624 | 1.0083 | 11.3757 | 11.62 | 1.8841 | 2.14 | 271 | 13.2338 | 0.064134 | 392 | 271.5 | 0 | 0.80884 | 1.1857e-05 | 0.7181 | 0.28315 | 0.010524 | 0.12108 | 0.79111 | 0.8275 | 0.82915 | 0.69608 | 0.032796 | 0 | 0.15489 | 44.8184 | 52.5946 | 1.9177 | 0.42111 | 0.093287 | 0.036966 | -0.01223 | 0.8339 | 0.82816 | 0.81446 | 0.81143 | 0.69548 | 0.42843 | 0.45648 | 0.15639 | 0.10453 | 0.10714 | 0.063162 | 0.054555 | 0.054592 | 0.80016 | 3.147 | 0.66643 | 0.43832 | 1.5967 | 0.33733 | 0.35673 | 1.5263 | 0.30863 | 0.80099 | 6.3594 | 0.66745 | 0.65128 | 5.1281 | 0.53507 | 0.76042 | 5.8282 | 0.61254 | 0.78086 | 38.0936 | 0.65619 | 0.77071 | 37.1453 | 0.64263 | 0.76968 | 37.063 | 0.64289 | 272 | 0.042553 | 0.028021 | 0.3843 | 0.0067453 | 0.80223 | 0.20597 | 0.11951
Text_H100_SeqLength_2048 | H_100 | 3600 | 0.8033 | 1.018 | 0.18971 | 0.8033 | 1.2673 | 0.77198 | 85.6422 | 13.4328 | 536 | 1.7048 | 0.91924 | 0.20611 | 0.71313 | 35.6564 | 1.0069 | 11.4904 | 11.64 | 1.9263 | 2.1 | 267 | 13.4029 | 0.03918 | 352 | 268 | 0 | 0.80419 | 1.2171e-05 | 0.7229 | 0.28569 | 0.0092759 | 0.12383 | 0.78922 | 0.82273 | 0.82536 | 0.70356 | 0.037152 | 0 | 0.081327 | 45.4803 | 51.9811 | 1.9466 | 0.41367 | 0.096993 | 0.081189 | 0.009089 | 0.83422 | 0.82427 | 0.81209 | 0.80857 | 0.68357 | 0.44018 | 0.46108 | 0.15539 | 0.10397 | 0.10652 | 0.062593 | 0.052909 | 0.053101 | 0.79943 | 3.3657 | 0.70053 | 0.43584 | 1.5818 | 0.33461 | 0.34234 | 1.49 | 0.30116 | 0.80769 | 6.6649 | 0.68652 | 0.66948 | 5.2965 | 0.55209 | 0.76206 | 5.8457 | 0.61561 | 0.78168 | 38.131 | 0.65897 | 0.7705 | 37.1378 | 0.64273 | 0.77098 | 37.3601 | 0.64354 | 268 | 0.065105 | 0.037152 | 0.39111 | 0.006674 | 0.80098 | 0.21051 | 0.11513
Text_H100_SeqLength_4096 | H_100 | 3600 | 0.8033 | 1.0237 | 0.19052 | 0.8033 | 1.2744 | 0.7737 | 85.56 | 13.4328 | 536 | 1.6363 | 0.9219 | 0.20549 | 0.71641 | 35.8205 | 1.0093 | 11.4909 | 11.72 | 1.9346 | 2.08 | 267 | 13.41 | 0.02735 | 420 | 268 | 0 | 0.81203 | 1.2868e-05 | 0.72564 | 0.29004 | 0.0082579 | 0.13842 | 0.79635 | 0.82771 | 0.82789 | 0.70697 | 0.035656 | 0 | 0.052026 | 45.5774 | 51.8231 | 2.0413 | 0.41035 | 0.095876 | 0.023626 | 0.0046555 | 0.83466 | 0.8248 | 0.81082 | 0.80848 | 0.67042 | 0.43573 | 0.4561 | 0.1579 | 0.1063 | 0.10889 | 0.061896 | 0.054168 | 0.054371 | 0.80222 | 3.2694 | 0.69039 | 0.43037 | 1.5561 | 0.32943 | 0.34375 | 1.4764 | 0.29688 | 0.80657 | 6.8827 | 0.70781 | 0.65569 | 5.1634 | 0.53915 | 0.76454 | 5.8831 | 0.61735 | 0.78424 | 38.2826 | 0.66174 | 0.77305 | 37.2604 | 0.64519 | 0.77337 | 37.5562 | 0.64745 | 268 | 0.05722 | 0.034566 | 0.39585 | 0.0054886 | 0.8125 | 0.21054 | 0.11812
Image_B200_BatchSize_128 | B_200 | 3600 | 0.8033 | 1.4935 | 0.49334 | 0.8033 | 1.8592 | 0.97643 | 30.1867 | 11.3924 | 632 | 1.8688 | 1.4602 | 0.50136 | 0.95879 | 47.9397 | 1.4895 | 3.422 | 3.48 | 7.9642 | 8.78 | 316 | 11.3863 | 0.05211 | 316 | 316 | 0 | 0.99473 | 0.00097525 | 0.97287 | 0.50794 | 0.014234 | 0.1402 | 0.9547 | 0.99602 | 0.99827 | 0.97175 | 0.043117 | 0 | 0.047497 | 73.9386 | 25.4308 | 0.50986 | 0.058211 | 0.014977 | 0.082049 | -0.016191 | 0.89747 | 0.8431 | 0.81738 | 0.81107 | 0.86701 | 0.90155 | 0.93311 | 0.15329 | 0.15111 | 0.15409 | 0.019614 | 0.018931 | 0.018931 | 0.99182 | 5.717 | 1.2012 | 0.70379 | 3.1637 | 0.68415 | 0.9342 | 3.8098 | 0.85571 | 0.98787 | 8.3786 | 0.93016 | 0.97316 | 7.8192 | 0.87176 | 0.97482 | 8.1026 | 0.90288 | 0.98142 | 48.5719 | 0.90461 | 0.97519 | 47.0025 | 0.87507 | 0.97521 | 46.796 | 0.87184 | 316 | 0.061526 | 0.041158 | 0.79884 | 0.0040458 | 0.8161 | 0.15872 | 0.092371
Image_B200_BatchSize_256 | B_200 | 3600 | 0.8033 | 1.7263 | 0.49824 | 0.8033 | 2.149 | 1.1885 | 23.8711 | 11.1111 | 647 | 2.3716 | 1.678 | 0.50382 | 1.1742 | 58.708 | 1.7052 | 2.6435 | 2.68 | 8.4886 | 9.28 | 323 | 11.1321 | 0.072785 | 323.5 | 323.5 | 323.5 | 1.2053 | 0.032033 | 1.18 | 0.53287 | 0.014925 | 1.1938 | 1.1938 | 1.2258 | 1.2266 | 1.1801 | 0.054767 | 0 | 0.032596 | 62.7865 | 35.5695 | 1.4669 | 0.10555 | 0.038932 | 1.1925 | 0.024075 | 0.91929 | 0.83831 | 0.81838 | 0.81395 | 1.0463 | 1.1918 | 1.2406 | 0.1911 | 0.20786 | 0.21311 | 0.034417 | 0.023579 | 0.023588 | 1.2032 | 6.9161 | 1.4957 | 0.77934 | 3.6564 | 0.80707 | 1.1187 | 4.4701 | 1.0104 | 1.2031 | 10.1176 | 1.1505 | 1.1746 | 9.4557 | 1.0797 | 1.1871 | 9.8459 | 1.1284 | 1.1918 | 59.499 | 1.1331 | 1.1879 | 57.2552 | 1.0917 | 1.1889 | 56.3409 | 1.074 | 321 | 0.88968 | 0.054767 | 0.78975 | 0.0044524 | 1.4283 | 0.32049 | 0.64936
Image_B200_BatchSize_512 | B_200 | 3600 | 0.8033 | 1.8597 | 0.4951 | 0.8033 | 2.315 | 1.3309 | 20.5644 | 11.1111 | 656 | 2.7176 | 1.8118 | 0.50181 | 1.31 | 65.5007 | 1.8527 | 2.2571 | 2.3 | 8.7276 | 9.1 | 328 | 10.9847 | 0.035334 | 328 | 328 | 328 | 1.3506 | 0.24452 | 1.3088 | 0.5284 | 0.014771 | 0.18328 | 1.307 | 1.3615 | 1.3615 | 1.3031 | 0.054536 | 0 | 0.018962 | 57.9039 | 40.8257 | 1.1347 | 0.090152 | 0.026503 | 0.0039665 | 0.023539 | 0.92846 | 0.8345 | 0.81617 | 0.81241 | 1.1707 | 1.4343 | 1.496 | 0.22239 | 0.25706 | 0.2642 | 0.047443 | 0.034691 | 0.034697 | 1.3518 | 7.6433 | 1.6812 | 0.84369 | 3.997 | 0.8941 | 1.2178 | 5.2302 | 1.2057 | 1.3474 | 11.2343 | 1.2924 | 1.3094 | 10.548 | 1.2173 | 1.3302 | 10.9821 | 1.2711 | 1.337 | 66.5981 | 1.2821 | 1.3305 | 64.1301 | 1.235 | 1.3307 | 64.171 | 1.2311 | 328 | 0.10548 | 0.052886 | 0.77037 | 0.0073462 | 1.3463 | 0.26346 | 0.10329
Image_B200_ImageSize_32 | B_200 | 3600 | 0.8033 | 1.4935 | 0.49334 | 0.8033 | 1.8592 | 0.97643 | 30.1867 | 11.3924 | 632 | 1.8688 | 1.4602 | 0.50136 | 0.95879 | 47.9397 | 1.4895 | 3.422 | 3.48 | 7.9642 | 8.78 | 316 | 11.3863 | 0.05211 | 316 | 316 | 0 | 0.99473 | 0.00097525 | 0.97287 | 0.50794 | 0.014234 | 0.1402 | 0.9547 | 0.99602 | 0.99827 | 0.97175 | 0.043117 | 0 | 0.047497 | 73.9386 | 25.4308 | 0.50986 | 0.058211 | 0.014977 | 0.082049 | -0.016191 | 0.89747 | 0.8431 | 0.81738 | 0.81107 | 0.86701 | 0.90155 | 0.93311 | 0.15329 | 0.15111 | 0.15409 | 0.019614 | 0.018931 | 0.018931 | 0.99182 | 5.717 | 1.2012 | 0.70379 | 3.1637 | 0.68415 | 0.9342 | 3.8098 | 0.85571 | 0.98787 | 8.3786 | 0.93016 | 0.97316 | 7.8192 | 0.87176 | 0.97482 | 8.1026 | 0.90288 | 0.98142 | 48.5719 | 0.90461 | 0.97519 | 47.0025 | 0.87507 | 0.97521 | 46.796 | 0.87184 | 316 | 0.061526 | 0.041158 | 0.79884 | 0.0040458 | 0.8161 | 0.15872 | 0.092371
Image_B200_ImageSize_64 | B_200 | 3600 | 0.8033 | 1.2394 | 0.32021 | 0.8033 | 1.5429 | 0.88915 | 52.9178 | 18.3673 | 392 | 1.6369 | 1.2062 | 0.32994 | 0.87627 | 43.8133 | 1.2244 | 9.7012 | 9.78 | 8.6651 | 9.1 | 196 | 18.3664 | 0.023299 | 200 | 195.5 | 0 | 0.90474 | 0.00011944 | 0.88835 | 0.70567 | 0.023076 | 0.21525 | 0.86593 | 0.91201 | 0.91389 | 0.88783 | 0.081374 | 0 | 0.023059 | 87.7175 | 11.8978 | 0.31887 | 0.032617 | 0.010097 | 0.21524 | 0.044598 | 0.90179 | 0.8538 | 0.81585 | 0.81763 | 0.76987 | 0.62732 | 0.64938 | 0.090059 | 0.07021 | 0.071961 | 0.0093193 | 0.0097672 | 0.0097672 | 0.89773 | 4.6531 | 0.96687 | 0.43356 | 1.6888 | 0.36587 | 0.38725 | 1.1806 | 0.24629 | 0.89535 | 9.6889 | 0.99799 | 0.84163 | 6.6362 | 0.73049 | 0.88388 | 6.6667 | 0.75954 | 0.89104 | 45.0897 | 0.83193 | 0.88882 | 42.8394 | 0.80124 | 0.88957 | 42.482 | 0.79541 | 392 | 0.16137 | 0.078068 | 0.88198 | 0.021021 | 0.64197 | 0.12331 | 0.073319
Image_B200_ImageSize_128 | B_200 | 3600 | 0.8033 | 0.921 | 0.25436 | 0.8033 | 1.1465 | 0.6465 | 86.0489 | 69.2308 | 112 | 0.85685 | 0.88477 | 0.26134 | 0.62343 | 31.1714 | 0.91732 | 54.9415 | 60.06 | 9.5057 | 11.06 | 55 | 63.98 | 0.28196 | 56 | 52 | 0 | 0.64656 | 9.1424e-08 | 0.63237 | 0.48386 | 0.028525 | 0.095732 | 0.61038 | 0.65784 | 0.6627 | 0.63097 | 0.094042 | 0 | 31.9189 | 60.8605 | 6.6043 | 0.24406 | 0.18916 | 0.18309 | 0.0062691 | -0.010155 | 0.82667 | 0.88459 | 0.82734 | 0.81293 | 0.55183 | 0.33587 | 0.34989 | 0.05452 | 0.041818 | 0.04203 | 0.04367 | 0.038349 | 0.038353 | 0.6472 | 2.3018 | 0.4889 | 0.12109 | 0.41273 | 0.085471 | 0.044688 | 0.19705 | 0.039415 | 0.64975 | 5.1962 | 0.53652 | 0.19058 | 1.2534 | 0.13069 | 0.045009 | 0.39791 | 0.039795 | 0.6499 | 31.3814 | 0.53714 | 0.56718 | 27.0006 | 0.46472 | 0.64689 | 30.6969 | 0.52835 | 116 | 0.033699 | 0.091933 | 0.5973 | 0.017776 | 0.47467 | 0.089711 | 0.046586
Image_B200_ModelSize_128 | B_200 | 3600 | 0.8033 | 1.4935 | 0.49334 | 0.8033 | 1.8592 | 0.97643 | 30.1867 | 11.3924 | 632 | 1.8688 | 1.4602 | 0.50136 | 0.95879 | 47.9397 | 1.4895 | 3.422 | 3.48 | 7.9642 | 8.78 | 316 | 11.3863 | 0.05211 | 316 | 316 | 0 | 0.99473 | 0.00097525 | 0.97287 | 0.50794 | 0.014234 | 0.1402 | 0.9547 | 0.99602 | 0.99827 | 0.97175 | 0.043117 | 0 | 0.047497 | 73.9386 | 25.4308 | 0.50986 | 0.058211 | 0.014977 | 0.082049 | -0.016191 | 0.89747 | 0.8431 | 0.81738 | 0.81107 | 0.86701 | 0.90155 | 0.93311 | 0.15329 | 0.15111 | 0.15409 | 0.019614 | 0.018931 | 0.018931 | 0.99182 | 5.717 | 1.2012 | 0.70379 | 3.1637 | 0.68415 | 0.9342 | 3.8098 | 0.85571 | 0.98787 | 8.3786 | 0.93016 | 0.97316 | 7.8192 | 0.87176 | 0.97482 | 8.1026 | 0.90288 | 0.98142 | 48.5719 | 0.90461 | 0.97519 | 47.0025 | 0.87507 | 0.97521 | 46.796 | 0.87184 | 316 | 0.061526 | 0.041158 | 0.79884 | 0.0040458 | 0.8161 | 0.15872 | 0.092371
Image_B200_ModelSize_256 | B_200 | 3600 | 0.8033 | 1.6961 | 0.44044 | 0.8033 | 2.1114 | 1.2325 | 27.96 | 21.9512 | 327 | 2.0857 | 1.6661 | 0.44722 | 1.2188 | 60.9425 | 1.6916 | 6.1114 | 6.18 | 15.8861 | 16.66 | 163 | 21.9975 | 0.065551 | 163.5 | 163.5 | 163.5 | 1.2507 | 0.03305 | 1.2313 | 0.9467 | 0.032521 | 1.2173 | 1.2223 | 1.2489 | 1.2522 | 1.2302 | 0.10104 | 0 | 0.12012 | 89.9932 | 9.417 | 0.39017 | 0.055105 | 0.02448 | 1.2173 | 0.027752 | 0.95315 | 0.88011 | 0.83607 | 0.81556 | 1.0755 | 1.1911 | 1.2438 | 0.10312 | 0.1092 | 0.1119 | 0.0063451 | 0.0080583 | 0.0080583 | 1.2426 | 9.0293 | 1.8762 | 0.50466 | 2.6729 | 0.5776 | 0.15396 | 0.42127 | 0.085127 | 1.243 | 15.1099 | 1.6396 | 0.84563 | 8.0256 | 0.9054 | 1.2137 | 9.4303 | 1.103 | 1.2383 | 62.4332 | 1.2281 | 1.2322 | 59.3875 | 1.1735 | 1.2315 | 59.869 | 1.1848 | 324 | 0.90856 | 0.10081 | 1.2142 | 0.016748 | 0.9866 | 0.37356 | 0.65762
Image_B200_ModelSize_512 | B_200 | 3600 | 0.8033 | 1.9175 | 0.42663 | 0.8033 | 2.387 | 1.4566 | 25.1356 | 56.25 | 135 | 1.8117 | 1.8714 | 0.43189 | 1.4395 | 71.9739 | 1.9053 | 13.4976 | 14.16 | 39.9618 | 43.362 | 67 | 53.2579 | 0.11186 | 67.5 | 67.5 | 64.5 | 1.4751 | 0.25389 | 1.4514 | 1.3998 | 0.094154 | 1.2948 | 1.4032 | 1.4794 | 1.4906 | 1.4508 | 0.14291 | 0 | 7.0407 | 85.9347 | 6.7707 | 0.19301 | 0.03806 | 0.022785 | 1.2948 | -0.010248 | 1.0083 | 0.92807 | 0.89534 | 0.84916 | 1.2041 | 1.5488 | 1.6143 | 0.058623 | 0.068953 | 0.070698 | 0.00068792 | 0.00029747 | 0.00029747 | 1.4678 | 11.9198 | 2.4817 | 0.2396 | 1.4715 | 0.31703 | 0.0063997 | 0.013851 | 0.0027702 | 1.4689 | 24.9995 | 2.5707 | 0.4576 | 5.1393 | 0.57563 | 0.022865 | 0.11852 | 0.012069 | 1.459 | 80.6514 | 1.6569 | 1.4565 | 70.2038 | 1.4669 | 1.4558 | 68.1041 | 1.4302 | 132 | 0.96429 | 0.11484 | 1.4476 | 0.052491 | 1.0591 | 0.51671 | 0.77236
Text_B200_BatchSize2 | B_200 | 3600 | 0.8033 | 0.91365 | 0.41787 | 0.8033 | 1.1374 | 0.44722 | 88.8667 | 17.3077 | 208 | 0.64722 | 0.84843 | 0.42714 | 0.42129 | 21.0645 | 0.89686 | 31.2322 | 34 | 3.5638 | 2.7 | 103 | 34.5527 | 0.15805 | 104 | 0 | 0 | 0.48639 | 4.1991e-10 | 0.43384 | 0.20661 | 0.073328 | 0.066628 | 0.41508 | 0.47316 | 0.48682 | 0.42758 | 0.24864 | 0 | 37.3093 | 34.0006 | 27.982 | 0.45967 | 0.20697 | 0.041462 | 0.022982 | 0.0040473 | 0.81233 | 0.83866 | 0.8257 | 0.8258 | 0.36723 | 0.23064 | 0.23479 | 0.039275 | 0.028754 | 0.028861 | 0.020303 | 0.01715 | 0.01715 | 0.45815 | 1.7197 | 0.35178 | 0.11379 | 0.41953 | 0.085327 | 0.045181 | 0.1914 | 0.038285 | 0.45204 | 3.6383 | 0.36816 | 0.17766 | 1.3673 | 0.13876 | 0.053852 | 0.4548 | 0.045488 | 0.43691 | 17.2822 | 0.29022 | 0.30452 | 14.5159 | 0.24451 | 0.33434 | 16.3188 | 0.27394 | 0 | 0.025756 | 0.22988 | 0.26089 | 0.053968 | 0.42737 | 0.088388 | 0.053772
Text_B200_BatchSize16 | B_200 | 3600 | 0.8033 | 1.0855 | 0.23672 | 0.8033 | 1.3513 | 0.79365 | 75.4422 | 8.4906 | 800 | 1.7844 | 0.99623 | 0.25886 | 0.73736 | 36.8682 | 1.0743 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 400 | 396 | 0 | 0.83718 | 1.6484e-05 | 0.78651 | 0.67937 | 0.15525 | 0.13726 | 0.81477 | 0.83067 | 0.83485 | 0.78521 | 0.6018 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 1.3682e-05 | 0.020177 | 0.8509 | 0.85872 | 0.84852 | 0.84782 | 0.73181 | 0.49566 | 0.5199 | 0.16717 | 0.11456 | 0.11754 | 0.064542 | 0.056811 | 0.057364 | 0.82275 | 3.4618 | 0.72788 | 0.54927 | 2.2012 | 0.46213 | 0.75317 | 2.7678 | 0.58771 | 0.80974 | 7.0507 | 0.73078 | 0.72568 | 6.1097 | 0.63639 | 0.77444 | 6.5815 | 0.68144 | 0.79293 | 40.5526 | 0.7033 | 0.73726 | 37.1055 | 0.6444 | 0.78407 | 39.5943 | 0.6885 | 400 | 0.0572 | 0.59078 | 0.76043 | 0.1196 | 0.85504 | 0.19547 | 0.088606
Text_B200_BatchSize32 | B_200 | 3600 | 0.8033 | 1.0267 | 0.2189 | 0.8033 | 1.2781 | 0.75138 | 81.3444 | 9.0909 | 808 | 1.8281 | 0.94352 | 0.26962 | 0.6739 | 33.6952 | 1.0176 | 7.2608 | 7.54 | 1.6564 | 1.9 | 403 | 8.9104 | 0.076621 | 408 | 399.5 | 0 | 0.77497 | 7.9339e-06 | 0.69814 | 0.21967 | 0.0079324 | 0.14505 | 0.77085 | 0.79444 | 0.79484 | 0.67928 | 0.024106 | 0 | 0.15471 | 1.1689 | 97.1631 | 0.98678 | 0.44353 | 0.082978 | 0.091847 | 0.00040899 | 0.83679 | 0.82847 | 0.81228 | 0.80873 | 0.66691 | 0.45704 | 0.47735 | 0.19433 | 0.13244 | 0.13575 | 0.15049 | 0.085168 | 0.089256 | 0.77747 | 3.2245 | 0.66894 | 0.55168 | 2.1069 | 0.44279 | 0.72635 | 2.5198 | 0.53973 | 0.77546 | 6.3878 | 0.664 | 0.74498 | 5.9839 | 0.6232 | 0.74669 | 6.0014 | 0.62234 | 0.75973 | 36.9367 | 0.64051 | 0.75184 | 36.2372 | 0.62912 | 0.75217 | 36.2289 | 0.62877 | 396 | 0.075734 | 0.022783 | 0.33609 | 0.0061243 | 0.8386 | 0.25354 | 0.10856
Text_B200_Deepspeedds_z1 | B_200 | 3600 | 0.8033 | 1.2096 | 0.24646 | 0.8033 | 1.5057 | 0.90666 | 70.1844 | 7.9646 | 824 | 2.2699 | 1.0356 | 0.26656 | 0.76904 | 38.4518 | 1.1995 | 6.1758 | 6.4 | 2.5715 | 2 | 411 | 8.7335 | 0.9838 | 416 | 411.5 | 0 | 0.91054 | 0.00011954 | 0.86108 | 0.71575 | 0.22645 | 0.36434 | 0.92242 | 0.94327 | 0.94869 | 0.84228 | 0.55764 | 0 | 29.0813 | 2.784 | 62.0211 | 5.59 | 0.43961 | 0.08395 | 0.36167 | 0.049411 | 0.86542 | 0.8891 | 0.87346 | 0.86855 | 0.82222 | 0.63164 | 0.65887 | 0.2462 | 0.19345 | 0.19806 | 0.18973 | 0.17384 | 0.17489 | 0.91899 | 4.3295 | 0.89917 | 0.67368 | 2.7973 | 0.59065 | 0.86764 | 3.314 | 0.70897 | 0.91108 | 8.44 | 0.87578 | 0.81308 | 6.9671 | 0.73336 | 0.89175 | 7.6298 | 0.80347 | 0.90241 | 47.3166 | 0.82856 | 0.88304 | 42.9306 | 0.75939 | 0.89524 | 46.2416 | 0.81092 | 421 | 0.27147 | 0.54026 | 0.80431 | 0.17522 | 1.0144 | 0.3856 | 0.18889
Text_B200_Deepspeedds_z2 | B_200 | 3600 | 0.8033 | 1.1046 | 0.24125 | 0.8033 | 1.3751 | 0.79644 | 74.5778 | 8.5714 | 815 | 1.78 | 1.0034 | 0.25986 | 0.7435 | 37.1752 | 1.0906 | 6.6051 | 6.9 | 2.1171 | 1.94 | 407 | 8.707 | 0.48509 | 407.5 | 396 | 0 | 0.8484 | 2.3169e-05 | 0.78621 | 0.58479 | 0.13165 | 0.5821 | 0.81481 | 0.84577 | 0.84629 | 0.78484 | 0.49169 | 0 | 19.7537 | 2.5003 | 76.5089 | 0.77496 | 0.38857 | 0.073518 | 0.58204 | 0.019315 | 0.85263 | 0.84863 | 0.84549 | 0.84268 | 0.70934 | 0.50169 | 0.51985 | 0.17304 | 0.11846 | 0.12159 | 0.076526 | 0.063197 | 0.06321 | 0.83425 | 3.5443 | 0.74093 | 0.57452 | 2.2747 | 0.47997 | 0.75952 | 2.7527 | 0.58898 | 0.82777 | 7.2246 | 0.74947 | 0.74967 | 6.2391 | 0.65312 | 0.78722 | 6.6268 | 0.69114 | 0.80205 | 40.5956 | 0.70764 | 0.79039 | 38.1299 | 0.66871 | 0.79001 | 39.6418 | 0.69134 | 396 | 0.43414 | 0.48373 | 0.76201 | 0.092023 | 0.87157 | 0.23777 | 0.33102
Text_B200_Deepspeedds_z3 | B_200 | 3600 | 0.8033 | 1.0855 | 0.23672 | 0.8033 | 1.3513 | 0.79365 | 75.4422 | 8.4906 | 800 | 1.7844 | 0.99623 | 0.25886 | 0.73736 | 36.8682 | 1.0743 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 400 | 396 | 0 | 0.83718 | 1.6484e-05 | 0.78651 | 0.67937 | 0.15525 | 0.13726 | 0.81477 | 0.83067 | 0.83485 | 0.78521 | 0.6018 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 1.3682e-05 | 0.020177 | 0.8509 | 0.85872 | 0.84852 | 0.84782 | 0.73181 | 0.49566 | 0.5199 | 0.16717 | 0.11456 | 0.11754 | 0.064542 | 0.056811 | 0.057364 | 0.82275 | 3.4618 | 0.72788 | 0.54927 | 2.2012 | 0.46213 | 0.75317 | 2.7678 | 0.58771 | 0.80974 | 7.0507 | 0.73078 | 0.72568 | 6.1097 | 0.63639 | 0.77444 | 6.5815 | 0.68144 | 0.79293 | 40.5526 | 0.7033 | 0.73726 | 37.1055 | 0.6444 | 0.78407 | 39.5943 | 0.6885 | 400 | 0.0572 | 0.59078 | 0.76043 | 0.1196 | 0.85504 | 0.19547 | 0.088606
Text_B200_Lamma_1B | B_200 | 3600 | 0.8033 | 1.2824 | 0.39846 | 0.8033 | 1.5964 | 0.83291 | 48.12 | 4.4776 | 1599 | 2.2717 | 1.1765 | 0.42359 | 0.75287 | 37.6435 | 1.2693 | 2.171 | 2.28 | 2.3326 | 2.522 | 799 | 4.5037 | 0.15552 | 799.5 | 792 | 0 | 0.85865 | 9.7964e-05 | 0.80476 | 0.19419 | 0.016371 | 0.59554 | 0.8335 | 0.87672 | 0.87687 | 0.79917 | 0.063052 | 0 | 0.4565 | 1.1689 | 97.0705 | 0.59672 | 0.59764 | 0.10968 | 0.59554 | -0.0081355 | 0.8643 | 0.82512 | 0.81552 | 0.81001 | 0.74074 | 0.64191 | 0.66278 | 0.32269 | 0.26397 | 0.26913 | 0.31144 | 0.25899 | 0.26451 | 0.86293 | 3.771 | 0.80706 | 0.81822 | 3.3016 | 0.70916 | 0.83017 | 3.3107 | 0.71299 | 0.85437 | 7.3392 | 0.78451 | 0.82941 | 6.6648 | 0.71632 | 0.83046 | 6.6401 | 0.71314 | 0.83842 | 40.8921 | 0.73224 | 0.83216 | 40.109 | 0.71916 | 0.83444 | 40.4247 | 0.72351 | 5 | 0.44798 | 0.058313 | 0.1203 | 0.0064838 | 0.97456 | 0.24228 | 0.33294
Text_B200_Lamma_3B | B_200 | 3600 | 0.8033 | 1.2347 | 0.31466 | 0.8033 | 1.5371 | 0.85785 | 56.9089 | 6.8702 | 1039 | 1.9574 | 1.1399 | 0.32804 | 0.81184 | 40.5919 | 1.219 | 4.2316 | 4.4 | 2.6954 | 2.7 | 519 | 6.9269 | 0.37202 | 520 | 515.5 | 0 | 0.89727 | 0.0001424 | 0.84591 | 0.309 | 0.070296 | 0.44144 | 0.85357 | 0.91638 | 0.9199 | 0.84612 | 0.24077 | 0 | 4.9876 | 1.7824 | 91.691 | 1.0999 | 0.38827 | 0.050956 | 0.42848 | 0.017605 | 0.87368 | 0.84055 | 0.83377 | 0.83101 | 0.75381 | 0.60466 | 0.62585 | 0.22403 | 0.17132 | 0.17507 | 0.21027 | 0.13891 | 0.14291 | 0.8929 | 4.2033 | 0.87203 | 0.80403 | 3.2792 | 0.7066 | 0.84499 | 3.2992 | 0.71532 | 0.88713 | 8.0424 | 0.85199 | 0.8269 | 6.7731 | 0.73084 | 0.85499 | 6.9377 | 0.75266 | 0.86407 | 42.7667 | 0.7692 | 0.85613 | 41.2757 | 0.74687 | 0.85649 | 41.9463 | 0.75713 | 9 | 0.31769 | 0.2304 | 0.49702 | 0.054909 | 1.1237 | 0.17671 | 0.22961
Text_B200_Lamma_8B | B_200 | 3600 | 0.8033 | 1.0855 | 0.23672 | 0.8033 | 1.3513 | 0.79365 | 75.4422 | 8.4906 | 800 | 1.7844 | 0.99623 | 0.25886 | 0.73736 | 36.8682 | 1.0743 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 400 | 396 | 0 | 0.83718 | 1.6484e-05 | 0.78651 | 0.67937 | 0.15525 | 0.13726 | 0.81477 | 0.83067 | 0.83485 | 0.78521 | 0.6018 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 1.3682e-05 | 0.020177 | 0.8509 | 0.85872 | 0.84852 | 0.84782 | 0.73181 | 0.49566 | 0.5199 | 0.16717 | 0.11456 | 0.11754 | 0.064542 | 0.056811 | 0.057364 | 0.82275 | 3.4618 | 0.72788 | 0.54927 | 2.2012 | 0.46213 | 0.75317 | 2.7678 | 0.58771 | 0.80974 | 7.0507 | 0.73078 | 0.72568 | 6.1097 | 0.63639 | 0.77444 | 6.5815 | 0.68144 | 0.79293 | 40.5526 | 0.7033 | 0.73726 | 37.1055 | 0.6444 | 0.78407 | 39.5943 | 0.6885 | 400 | 0.0572 | 0.59078 | 0.76043 | 0.1196 | 0.85504 | 0.19547 | 0.088606
Text_B200_SeqLength_1024 | B_200 | 3600 | 0.8033 | 1.0842 | 0.23792 | 0.8033 | 1.3497 | 0.78762 | 75.46 | 8.7379 | 792 | 1.8029 | 0.99603 | 0.25861 | 0.73742 | 36.8709 | 1.0749 | 6.8683 | 7.03 | 2.1257 | 2.04 | 396 | 8.994 | 0.3737 | 404 | 396 | 0 | 0.8311 | 2.128e-05 | 0.76731 | 0.28897 | 0.10404 | 0.13832 | 0.80828 | 0.83217 | 0.83597 | 0.76322 | 0.37703 | 0 | 15.1867 | 2.5589 | 80.8655 | 0.9394 | 0.38934 | 0.06008 | 0.0043776 | 0.014093 | 0.85044 | 0.8441 | 0.83765 | 0.83416 | 0.73037 | 0.49863 | 0.51978 | 0.17067 | 0.11603 | 0.11907 | 0.073517 | 0.06119 | 0.061565 | 0.81499 | 3.5064 | 0.72776 | 0.57724 | 2.262 | 0.47756 | 0.75581 | 2.6932 | 0.57664 | 0.81149 | 7.1095 | 0.73827 | 0.75416 | 6.2233 | 0.65191 | 0.78181 | 6.5353 | 0.68355 | 0.79386 | 39.6817 | 0.69413 | 0.78506 | 37.8588 | 0.66507 | 0.78584 | 38.9428 | 0.67964 | 404 | 0.059143 | 0.36809 | 0.44012 | 0.073053 | 0.84557 | 0.19207 | 0.091471
Text_B200_SeqLength_2048 | B_200 | 3600 | 0.8033 | 1.0855 | 0.23672 | 0.8033 | 1.3513 | 0.79365 | 75.4422 | 8.4906 | 800 | 1.7844 | 0.99623 | 0.25886 | 0.73736 | 36.8682 | 1.0743 | 6.7944 | 7 | 2.0573 | 1.82 | 400 | 8.8515 | 0.58824 | 400 | 396 | 0 | 0.83718 | 1.6484e-05 | 0.78651 | 0.67937 | 0.15525 | 0.13726 | 0.81477 | 0.83067 | 0.83485 | 0.78521 | 0.6018 | 0 | 25.0785 | 2.9012 | 70.5984 | 1.0454 | 0.31777 | 0.058734 | 1.3682e-05 | 0.020177 | 0.8509 | 0.85872 | 0.84852 | 0.84782 | 0.73181 | 0.49566 | 0.5199 | 0.16717 | 0.11456 | 0.11754 | 0.064542 | 0.056811 | 0.057364 | 0.82275 | 3.4618 | 0.72788 | 0.54927 | 2.2012 | 0.46213 | 0.75317 | 2.7678 | 0.58771 | 0.80974 | 7.0507 | 0.73078 | 0.72568 | 6.1097 | 0.63639 | 0.77444 | 6.5815 | 0.68144 | 0.79293 | 40.5526 | 0.7033 | 0.73726 | 37.1055 | 0.6444 | 0.78407 | 39.5943 | 0.6885 | 400 | 0.0572 | 0.59078 | 0.76043 | 0.1196 | 0.85504 | 0.19547 | 0.088606
Text_B200_SeqLength_4096 | B_200 | 3600 | 0.8033 | 1.0846 | 0.23696 | 0.8033 | 1.3502 | 0.78805 | 75.2956 | 8.6538 | 792 | 1.8167 | 0.99561 | 0.25852 | 0.73709 | 36.8546 | 1.0747 | 6.8543 | 6.985 | 2.1246 | 2.08 | 396 | 8.9789 | 0.43277 | 403.5 | 396 | 0 | 0.82669 | 1.995e-05 | 0.76961 | 0.34214 | 0.1147 | 0.47035 | 0.81082 | 0.82862 | 0.83084 | 0.76628 | 0.42089 | 0 | 17.8616 | 2.5654 | 78.1502 | 0.98671 | 0.36748 | 0.068649 | 0.47035 | 0.020349 | 0.85066 | 0.84505 | 0.83794 | 0.8374 | 0.7035 | 0.49225 | 0.50852 | 0.16921 | 0.11456 | 0.11758 | 0.06737 | 0.05795 | 0.05797 | 0.81629 | 3.4849 | 0.72542 | 0.56095 | 2.2005 | 0.46444 | 0.75635 | 2.7239 | 0.58288 | 0.81026 | 7.0401 | 0.72978 | 0.74817 | 6.1987 | 0.64903 | 0.78197 | 6.5244 | 0.68081 | 0.79352 | 39.8991 | 0.69617 | 0.78513 | 37.8617 | 0.66451 | 0.78538 | 38.9229 | 0.67935 | 400 | 0.34968 | 0.41704 | 0.43599 | 0.077525 | 0.87039 | 0.21923 | 0.29402

## Electrical_characteristics
scenario | I_IGBT_rms_A | I_IGBT_peak_A | I_Diode_rms_A | I_Diode_peak_A | P_loss_IGBT_mean_W | P_loss_IGBT_max_W | P_loss_IGBT_swing_W | P_loss_Diode_mean_W | P_loss_Diode_max_W | P_loss_Diode_swing_W | Switching_share_pct | Diode_share_pct | Loss_ratio_pct
Image_B200_BatchSize_128 | 413.1867 | 1458.5026 | 122.4976 | 338.6459 | 346.7291 | 671.2682 | 455.8769 | 28.8584 | 55.1442 | 37.0047 | 49.0072 | 7.6835 | 0.046755
Image_B200_BatchSize_256 | 423.2325 | 1685.8082 | 125.4759 | 391.4234 | 348.1692 | 790.4809 | 564.2375 | 28.939 | 64.5554 | 45.5654 | 48.8096 | 7.6739 | 0.046945
Image_B200_BatchSize_512 | 427.453 | 1816.0735 | 126.7271 | 421.6694 | 348.7845 | 860.5742 | 638.521 | 28.9734 | 70.0481 | 51.3986 | 48.7256 | 7.6698 | 0.047025
Image_B200_ImageSize_128 | 380.5889 | 899.4174 | 112.8333 | 208.8334 | 342.2944 | 394.7977 | 282.9049 | 28.6101 | 32.9336 | 23.4412 | 49.626 | 7.7136 | 0.046172
Image_B200_ImageSize_32 | 413.1867 | 1458.5026 | 122.4976 | 338.6459 | 346.7291 | 671.2682 | 455.8769 | 28.8584 | 55.1442 | 37.0047 | 49.0072 | 7.6835 | 0.046755
Image_B200_ImageSize_64 | 415.1771 | 1210.3467 | 123.0877 | 281.0273 | 347.0117 | 545.6148 | 401.2265 | 28.8742 | 45.1213 | 32.9188 | 48.9683 | 7.6816 | 0.046792
Image_B200_ModelSize_128 | 413.1867 | 1458.5026 | 122.4976 | 338.6459 | 346.7291 | 671.2682 | 455.8769 | 28.8584 | 55.1442 | 37.0047 | 49.0072 | 7.6835 | 0.046755
Image_B200_ModelSize_256 | 438.8191 | 1656.3606 | 130.0968 | 384.5861 | 350.4721 | 774.8149 | 582.0592 | 29.0679 | 63.3237 | 47.0804 | 48.4968 | 7.6587 | 0.047247
Image_B200_ModelSize_512 | 464.2308 | 1872.5669 | 137.6306 | 434.7865 | 354.4051 | 891.3741 | 697.9813 | 29.2881 | 72.4527 | 56.2056 | 47.9719 | 7.6332 | 0.047764
Image_H100_BatchSize_128 | 424.7443 | 1513.8516 | 125.9241 | 351.4973 | 348.3889 | 699.934 | 490.0576 | 28.9513 | 57.4155 | 39.7901 | 48.7796 | 7.6725 | 0.046973
Image_H100_BatchSize_256 | 401.6096 | 1186.5471 | 119.0653 | 275.5013 | 345.1124 | 533.8104 | 332.4756 | 28.7679 | 44.1738 | 27.1847 | 49.231 | 7.6944 | 0.046543
Image_H100_BatchSize_512 | 437.0793 | 1953.1287 | 129.581 | 453.4919 | 350.2109 | 935.7165 | 730.1719 | 29.0533 | 75.9053 | 58.6516 | 48.5321 | 7.6604 | 0.047213
Image_H100_ImageSize_16 | 395.896 | 1283.4068 | 117.3714 | 297.9909 | 344.3315 | 582.1214 | 335.0751 | 28.7242 | 48.0448 | 27.2722 | 49.3398 | 7.6997 | 0.04644
Image_H100_ImageSize_32 | 424.7443 | 1513.8516 | 125.9241 | 351.4973 | 348.3889 | 699.934 | 490.0576 | 28.9513 | 57.4155 | 39.7901 | 48.7796 | 7.6725 | 0.046973
Image_H100_ImageSize_64 | 410.7055 | 1103.77 | 121.762 | 256.2815 | 346.3788 | 493.0898 | 387.0979 | 28.8388 | 40.8973 | 31.9075 | 49.0555 | 7.6859 | 0.046709
Image_H100_ModelSize_128 | 424.7443 | 1513.8516 | 125.9241 | 351.4973 | 348.3889 | 699.934 | 490.0576 | 28.9513 | 57.4155 | 39.7901 | 48.7796 | 7.6725 | 0.046973
Image_H100_ModelSize_256 | 455.295 | 1651.4336 | 134.9814 | 383.4421 | 352.9968 | 772.2002 | 605.7876 | 29.2092 | 63.118 | 49.0847 | 48.1586 | 7.6423 | 0.047579
Image_H100_ModelSize_512 | 480.7117 | 1896.8528 | 142.5167 | 440.4253 | 357.0742 | 904.6894 | 724.2578 | 29.4375 | 73.4906 | 58.3996 | 47.6221 | 7.6162 | 0.048115
Text_B200_BatchSize16 | 391.7435 | 1060.0526 | 116.1403 | 246.1309 | 343.7709 | 471.7946 | 350.7802 | 28.6928 | 39.1786 | 28.9716 | 49.4182 | 7.7035 | 0.046366
Text_B200_BatchSize2 | 373.9903 | 892.239 | 110.877 | 207.1667 | 341.441 | 391.4028 | 197.8929 | 28.5624 | 32.6571 | 16.3383 | 49.7468 | 7.7195 | 0.04606
Text_B200_BatchSize32 | 385.2493 | 1002.6606 | 114.215 | 232.8052 | 342.9061 | 444.0593 | 330.303 | 28.6444 | 36.9348 | 27.3281 | 49.5397 | 7.7094 | 0.046253
Text_B200_Deepspeedds_z1 | 398.4304 | 1181.2045 | 118.1228 | 274.2608 | 344.6765 | 531.1664 | 404.7848 | 28.7435 | 43.9614 | 33.3239 | 49.2917 | 7.6974 | 0.046485
Text_B200_Deepspeedds_z2 | 392.5437 | 1078.7098 | 116.3775 | 250.4628 | 343.8785 | 480.8649 | 352.4728 | 28.6988 | 39.9111 | 29.0991 | 49.4032 | 7.7028 | 0.046381
Text_B200_Deepspeedds_z3 | 391.7435 | 1060.0526 | 116.1403 | 246.1309 | 343.7709 | 471.7946 | 350.7802 | 28.6928 | 39.1786 | 28.9716 | 49.4182 | 7.7035 | 0.046366
Text_B200_Lamma_1B | 397.9142 | 1252.3271 | 117.9698 | 290.7746 | 344.606 | 566.5418 | 378.8949 | 28.7395 | 46.7984 | 31.0072 | 49.3015 | 7.6978 | 0.046476
Text_B200_Lamma_3B | 402.2354 | 1205.7843 | 119.2509 | 279.9679 | 345.1986 | 543.3485 | 385.9904 | 28.7727 | 44.9394 | 31.6978 | 49.219 | 7.6938 | 0.046554
Text_B200_Lamma_8B | 391.7435 | 1060.0526 | 116.1403 | 246.1309 | 343.7709 | 471.7946 | 350.7802 | 28.6928 | 39.1786 | 28.9716 | 49.4182 | 7.7035 | 0.046366
Text_B200_SeqLength_1024 | 391.5319 | 1058.7742 | 116.0776 | 245.834 | 343.7425 | 471.174 | 348.3022 | 28.6912 | 39.1285 | 28.762 | 49.4222 | 7.7037 | 0.046363
Text_B200_SeqLength_2048 | 391.7435 | 1060.0526 | 116.1403 | 246.1309 | 343.7709 | 471.7946 | 350.7802 | 28.6928 | 39.1786 | 28.9716 | 49.4182 | 7.7035 | 0.046366
Text_B200_SeqLength_4096 | 391.6364 | 1059.1816 | 116.1086 | 245.9286 | 343.7565 | 471.3718 | 348.4775 | 28.692 | 39.1445 | 28.7768 | 49.4202 | 7.7036 | 0.046365
Text_H100_BatchSize16 | 384.0682 | 994.1323 | 113.8648 | 230.825 | 342.7504 | 439.9593 | 337.7796 | 28.6357 | 36.6025 | 27.9889 | 49.5616 | 7.7105 | 0.046232
Text_H100_BatchSize2 | 375.2941 | 923.3005 | 111.2636 | 214.3787 | 341.6085 | 406.1211 | 229.5998 | 28.5717 | 33.8552 | 18.9716 | 49.7231 | 7.7183 | 0.046082
Text_H100_BatchSize32 | 382.5423 | 973.7871 | 113.4124 | 226.1011 | 342.5499 | 430.2008 | 334.5476 | 28.6244 | 35.8112 | 27.7354 | 49.5899 | 7.7119 | 0.046206
Text_H100_Deepspeedds_z1 | 395.8351 | 1124.1496 | 117.3533 | 261.0134 | 344.3232 | 503.0668 | 409.0953 | 28.7237 | 41.7012 | 33.7455 | 49.341 | 7.6998 | 0.046439
Text_H100_Deepspeedds_z2 | 384.9575 | 1020.0735 | 114.1285 | 236.8482 | 342.8676 | 452.4478 | 342.2732 | 28.6422 | 37.6141 | 28.3474 | 49.5451 | 7.7097 | 0.046248
Text_H100_Deepspeedds_z3 | 384.0682 | 994.1323 | 113.8648 | 230.825 | 342.7504 | 439.9593 | 337.7796 | 28.6357 | 36.6025 | 27.9889 | 49.5616 | 7.7105 | 0.046232
Text_H100_Lamma_1B | 409.7009 | 1331.021 | 121.4641 | 309.0463 | 346.2375 | 606.1321 | 454.7578 | 28.8309 | 49.9624 | 37.2524 | 49.075 | 7.6868 | 0.046691
Text_H100_Lamma_3B | 398.455 | 1127.1708 | 118.1301 | 261.7149 | 344.6799 | 504.5485 | 385.9062 | 28.7437 | 41.8206 | 31.8356 | 49.2912 | 7.6973 | 0.046486
Text_H100_Lamma_8B | 384.0682 | 994.1323 | 113.8648 | 230.825 | 342.7504 | 439.9593 | 337.7796 | 28.6357 | 36.6025 | 27.9889 | 49.5616 | 7.7105 | 0.046232
Text_H100_SeqLength_1024 | 383.9183 | 999.1236 | 113.8204 | 231.9839 | 342.7306 | 442.3582 | 337.5914 | 28.6346 | 36.7969 | 27.9733 | 49.5644 | 7.7106 | 0.04623
Text_H100_SeqLength_2048 | 384.0682 | 994.1323 | 113.8648 | 230.825 | 342.7504 | 439.9593 | 337.7796 | 28.6357 | 36.6025 | 27.9889 | 49.5616 | 7.7105 | 0.046232
Text_H100_SeqLength_4096 | 384.2681 | 999.7159 | 113.9241 | 232.1214 | 342.7767 | 442.643 | 338.6062 | 28.6371 | 36.82 | 28.0555 | 49.5579 | 7.7103 | 0.046236

## Thermal_characteristics
scenario | Tj_IGBT_mean_C | Tj_IGBT_max_C | Tj_IGBT_min_C | Tj_IGBT_swing_K | Tj_Diode_mean_C | Tj_Diode_max_C | Tj_Diode_min_C | Tj_Diode_swing_K | T_case_mean_C | T_case_swing_K | IGBT_cycles_per_h | IGBT_dT_max_K | IGBT_dT_mean_K | IGBT_dT_p95_K | IGBT_cycles_dT_lt5_per_h | IGBT_cycles_dT_5_10_per_h | IGBT_cycles_dT_10_20_per_h | IGBT_cycles_dT_ge20_per_h | IGBT_cycle_Tmean_C | IGBT_cycle_duration_mean_s | IGBT_cycle_duration_p95_s | IGBT_grid_cycles_per_h | IGBT_grid_cycle_dT_mean_K | IGBT_grid_cycle_dT_max_K | IGBT_load_cycles_per_h | IGBT_load_cycle_dT_mean_K | IGBT_load_cycle_dT_max_K | IGBT_load_cycle_Tmean_C | IGBT_load_cycle_duration_mean_s | IGBT_burst_cycles_per_h | IGBT_burst_dT_mean_K | IGBT_burst_dT_median_K | IGBT_burst_dT_p95_K | IGBT_burst_dT_max_K | IGBT_burst_dT_eq_K | IGBT_burst_Tmean_C | IGBT_burst_duration_mean_s | Diode_cycles_per_h | Diode_dT_max_K | Diode_dT_mean_K | Diode_dT_p95_K | Diode_cycles_dT_lt5_per_h | Diode_cycles_dT_5_10_per_h | Diode_cycles_dT_10_20_per_h | Diode_cycles_dT_ge20_per_h | Diode_cycle_Tmean_C | Diode_cycle_duration_mean_s | Diode_cycle_duration_p95_s | Diode_grid_cycles_per_h | Diode_grid_cycle_dT_mean_K | Diode_grid_cycle_dT_max_K | Diode_load_cycles_per_h | Diode_load_cycle_dT_mean_K | Diode_load_cycle_dT_max_K | Diode_load_cycle_Tmean_C | Diode_load_cycle_duration_mean_s | Diode_burst_cycles_per_h | Diode_burst_dT_mean_K | Diode_burst_dT_median_K | Diode_burst_dT_p95_K | Diode_burst_dT_max_K | Diode_burst_dT_eq_K | Diode_burst_Tmean_C | Diode_burst_duration_mean_s
Image_B200_BatchSize_128 | 106.4341 | 140.1928 | 40 | 77.3745 | 101.4596 | 130.188 | 40 | 75.8499 | 100.387 | 75.6287 | 180000.5 | 100.1928 | 0.74331 | 1.4213 | 179684.5 | 315.5 | 0 | 0.5 | 106.4535 | 0.030984 | 0.013 | 179136 | 0.72906 | 1.4419 | 864.5 | 3.6954 | 100.1928 | 106.8379 | 4.3767 | 315.5 | 8.534 | 8.5452 | 8.713 | 8.7749 | 8.5451 | 108.2112 | 5.7563 | 180000 | 90.188 | 0.16035 | 0.30178 | 179999.5 | 0 | 0 | 0.5 | 101.4608 | 0.029214 | 0.012 | 179132.5 | 0.15792 | 0.30582 | 867.5 | 0.66374 | 90.188 | 107.4114 | 3.8436 | 0
Image_B200_BatchSize_256 | 106.7107 | 142.3546 | 40 | 77.8207 | 101.7143 | 130.7705 | 40 | 76.1797 | 100.6388 | 76.0542 | 180000.5 | 102.3546 | 0.74669 | 1.6565 | 179677 | 0 | 323 | 0.5 | 106.7303 | 0.030843 | 0.013 | 179139 | 0.72917 | 1.6816 | 861.5 | 4.3899 | 102.3546 | 106.0968 | 4.3807 | 323 | 10.4459 | 10.4673 | 10.5949 | 10.7 | 10.4545 | 109.4336 | 5.5578 | 180000 | 90.7705 | 0.16082 | 0.34965 | 179999.5 | 0 | 0 | 0.5 | 101.7155 | 0.02924 | 0.012 | 178992.5 | 0.15775 | 0.35462 | 1007.5 | 0.706 | 90.7705 | 107.2718 | 3.3104 | 0
Image_B200_BatchSize_512 | 106.8161 | 143.971 | 40 | 77.7274 | 101.81 | 131.1883 | 40 | 76.2597 | 100.7332 | 75.9651 | 180000.5 | 103.971 | 0.74814 | 1.8122 | 179672.5 | 0 | 327.5 | 0.5 | 106.8358 | 0.031967 | 0.013 | 178834.5 | 0.7277 | 1.8501 | 1166 | 3.8826 | 103.971 | 106.7264 | 3.4485 | 327.5 | 11.786 | 11.8061 | 11.9565 | 12.0427 | 11.7944 | 110.142 | 5.6383 | 180000 | 91.1883 | 0.16102 | 0.38122 | 179999.5 | 0 | 0 | 0.5 | 101.8111 | 0.030267 | 0.012 | 178677 | 0.15747 | 0.38824 | 1323 | 0.64123 | 91.1883 | 105.2522 | 2.6777 | 0
Image_B200_ImageSize_128 | 105.631 | 134.1233 | 40 | 75.4961 | 100.725 | 128.2355 | 40 | 74.9957 | 99.6613 | 74.9943 | 180000.5 | 94.1233 | 0.73289 | 0.82509 | 179948 | 52 | 0 | 0.5 | 105.6497 | 0.037716 | 0.013 | 174454.5 | 0.72465 | 0.83488 | 5546 | 0.99227 | 94.1233 | 105.0629 | 0.90703 | 52 | 5.3496 | 5.3873 | 5.5121 | 5.5244 | 5.3688 | 104.2351 | 7.871 | 180000 | 88.2355 | 0.15891 | 0.17891 | 179999.5 | 0 | 0 | 0.5 | 100.7261 | 0.03146 | 0.012 | 173689 | 0.15726 | 0.18106 | 6311 | 0.20438 | 88.2355 | 102.5588 | 0.6087 | 0
Image_B200_ImageSize_32 | 106.4341 | 140.1928 | 40 | 77.3745 | 101.4596 | 130.188 | 40 | 75.8499 | 100.387 | 75.6287 | 180000.5 | 100.1928 | 0.74331 | 1.4213 | 179684.5 | 315.5 | 0 | 0.5 | 106.4535 | 0.030984 | 0.013 | 179136 | 0.72906 | 1.4419 | 864.5 | 3.6954 | 100.1928 | 106.8379 | 4.3767 | 315.5 | 8.534 | 8.5452 | 8.713 | 8.7749 | 8.5451 | 108.2112 | 5.7563 | 180000 | 90.188 | 0.16035 | 0.30178 | 179999.5 | 0 | 0 | 0.5 | 101.4608 | 0.029214 | 0.012 | 179132.5 | 0.15792 | 0.30582 | 867.5 | 0.66374 | 90.188 | 107.4114 | 3.8436 | 0
Image_B200_ImageSize_64 | 106.5566 | 137.9535 | 40 | 77.5536 | 101.5776 | 129.852 | 40 | 75.6705 | 100.5043 | 75.8131 | 180000.5 | 97.9535 | 0.74397 | 1.1463 | 179804.5 | 195.5 | 0 | 0.5 | 106.576 | 0.029839 | 0.013 | 178539.5 | 0.73465 | 1.1597 | 1461 | 1.883 | 97.9535 | 110.7493 | 2.3495 | 195.5 | 7.5248 | 7.5463 | 7.6736 | 7.7559 | 7.5366 | 106.5435 | 6.4495 | 180000 | 89.852 | 0.16045 | 0.24514 | 179999.5 | 0 | 0 | 0.5 | 101.5787 | 0.027462 | 0.012 | 179319 | 0.15905 | 0.24774 | 681 | 0.52808 | 89.852 | 104.7089 | 4.3818 | 0
Image_B200_ModelSize_128 | 106.4341 | 140.1928 | 40 | 77.3745 | 101.4596 | 130.188 | 40 | 75.8499 | 100.387 | 75.6287 | 180000.5 | 100.1928 | 0.74331 | 1.4213 | 179684.5 | 315.5 | 0 | 0.5 | 106.4535 | 0.030984 | 0.013 | 179136 | 0.72906 | 1.4419 | 864.5 | 3.6954 | 100.1928 | 106.8379 | 4.3767 | 315.5 | 8.534 | 8.5452 | 8.713 | 8.7749 | 8.5451 | 108.2112 | 5.7563 | 180000 | 90.188 | 0.16035 | 0.30178 | 179999.5 | 0 | 0 | 0.5 | 101.4608 | 0.029214 | 0.012 | 179132.5 | 0.15792 | 0.30582 | 867.5 | 0.66374 | 90.188 | 107.4114 | 3.8436 | 0
Image_B200_ModelSize_256 | 107.1021 | 142.8541 | 40 | 79.7459 | 102.0704 | 131.338 | 40 | 76.7454 | 100.9902 | 76.6033 | 180000.5 | 102.8541 | 0.7521 | 1.646 | 179837 | 0 | 163 | 0.5 | 107.122 | 0.031886 | 0.013 | 178976 | 0.7417 | 1.6808 | 1024.5 | 2.5693 | 102.8541 | 107.9291 | 3.8874 | 163 | 10.9004 | 10.9466 | 11.1733 | 11.3335 | 10.9243 | 109.6485 | 11.2689 | 180003 | 91.338 | 0.16157 | 0.34699 | 180002.5 | 0 | 0 | 0.5 | 102.0716 | 0.031147 | 0.012 | 179233.5 | 0.15984 | 0.3524 | 769.5 | 0.56428 | 91.338 | 103.7702 | 4.8631 | 0
Image_B200_ModelSize_512 | 107.7688 | 146.6319 | 40 | 81.6102 | 102.6759 | 133.3076 | 40 | 78.1247 | 101.5879 | 77.7652 | 180000.5 | 106.6319 | 0.76134 | 1.8786 | 179932.5 | 4 | 63.5 | 0.5 | 107.7893 | 0.033368 | 0.013 | 176964.5 | 0.73934 | 1.9526 | 3036 | 2.0439 | 106.6319 | 115.0123 | 1.4537 | 67.5 | 13.1502 | 13.493 | 14.082 | 14.1724 | 13.497 | 110.8896 | 29.5002 | 180000 | 93.3076 | 0.16285 | 0.39376 | 179999.5 | 0 | 0 | 0.5 | 102.6771 | 0.032155 | 0.012 | 179123 | 0.1611 | 0.40686 | 877 | 0.52089 | 93.3076 | 110.8873 | 4.4759 | 0
Image_H100_BatchSize_128 | 106.7189 | 141.0667 | 40 | 78.5131 | 101.7192 | 130.6145 | 40 | 76.0659 | 100.6432 | 75.9738 | 180000.5 | 101.0667 | 0.7472 | 1.4562 | 179768 | 232 | 0 | 0.5 | 106.7385 | 0.031755 | 0.013 | 179049 | 0.73468 | 1.5034 | 951.5 | 3.1041 | 101.0667 | 105.8221 | 4.1802 | 232 | 9.0547 | 9.1082 | 9.5336 | 9.661 | 9.1554 | 108.6635 | 8.414 | 180000 | 90.6145 | 0.16089 | 0.30872 | 179999.5 | 0 | 0 | 0.5 | 101.7203 | 0.030924 | 0.012 | 179197.5 | 0.15882 | 0.31856 | 802.5 | 0.62377 | 90.6145 | 106.6731 | 4.6047 | 0
Image_H100_BatchSize_256 | 106.1188 | 137.2976 | 40 | 76.8025 | 101.1695 | 129.3 | 40 | 75.4578 | 100.1002 | 75.1216 | 180000.5 | 97.2976 | 0.73951 | 1.1333 | 179801 | 199 | 0 | 0.5 | 106.1379 | 0.030906 | 0.013 | 177330.5 | 0.72869 | 1.1554 | 2670 | 1.458 | 97.2976 | 109.6373 | 1.3978 | 199 | 6.3557 | 6.3888 | 6.5353 | 6.5932 | 6.3773 | 106.5213 | 7.4983 | 180003 | 89.3 | 0.15982 | 0.24245 | 180002.5 | 0 | 0 | 0.5 | 101.1707 | 0.029139 | 0.012 | 179000.5 | 0.15853 | 0.2458 | 1002.5 | 0.39176 | 89.3 | 109.6444 | 3.2941 | 0
Image_H100_BatchSize_512 | 106.8414 | 146.2724 | 40 | 78.5267 | 101.8134 | 132.3367 | 40 | 77.5162 | 100.7341 | 77.2239 | 180000.5 | 106.2724 | 0.7515 | 1.972 | 179760.5 | 84 | 155.5 | 0.5 | 106.8613 | 0.032313 | 0.013 | 177895.5 | 0.73028 | 2.0269 | 2105 | 2.5443 | 106.2724 | 109.6765 | 1.9719 | 239.5 | 11.0787 | 13.42 | 13.7455 | 13.8351 | 13.1681 | 110.0387 | 7.8725 | 180000 | 92.3367 | 0.16149 | 0.41331 | 179999.5 | 0 | 0 | 0.5 | 101.8146 | 0.031779 | 0.012 | 178035 | 0.15811 | 0.42564 | 1965 | 0.46707 | 92.3367 | 104.787 | 1.9638 | 0
Image_H100_ImageSize_16 | 105.9667 | 138.0255 | 40 | 76.1665 | 101.0294 | 129.3379 | 40 | 75.4709 | 99.9616 | 75.3354 | 180000.5 | 98.0255 | 0.73768 | 1.2261 | 179702 | 298 | 0 | 0.5 | 105.9857 | 0.031458 | 0.013 | 178516 | 0.72752 | 1.2512 | 1484.5 | 1.9589 | 98.0255 | 108.3042 | 2.6053 | 298 | 6.3702 | 6.3961 | 6.5838 | 6.6776 | 6.4024 | 107.4997 | 5.81 | 180000 | 89.3379 | 0.15957 | 0.26185 | 179999.5 | 0 | 0 | 0.5 | 101.0305 | 0.029364 | 0.012 | 178978.5 | 0.15777 | 0.26614 | 1021.5 | 0.47595 | 89.3379 | 110.3477 | 3.2779 | 0
Image_H100_ImageSize_32 | 106.7189 | 141.0667 | 40 | 78.5131 | 101.7192 | 130.6145 | 40 | 76.0659 | 100.6432 | 75.9738 | 180000.5 | 101.0667 | 0.7472 | 1.4562 | 179768 | 232 | 0 | 0.5 | 106.7385 | 0.031755 | 0.013 | 179049 | 0.73468 | 1.5034 | 951.5 | 3.1041 | 101.0667 | 105.8221 | 4.1802 | 232 | 9.0547 | 9.1082 | 9.5336 | 9.661 | 9.1554 | 108.6635 | 8.414 | 180000 | 90.6145 | 0.16089 | 0.30872 | 179999.5 | 0 | 0 | 0.5 | 101.7203 | 0.030924 | 0.012 | 179197.5 | 0.15882 | 0.31856 | 802.5 | 0.62377 | 90.6145 | 106.6731 | 4.6047 | 0
Image_H100_ImageSize_64 | 106.4258 | 136.902 | 40 | 77.2536 | 101.4568 | 129.564 | 40 | 75.6921 | 100.3848 | 75.7391 | 179997.5 | 96.902 | 0.7425 | 1.0451 | 179822 | 175 | 0 | 0.5 | 106.445 | 0.031078 | 0.013 | 172935 | 0.72419 | 1.0691 | 7062.5 | 1.191 | 96.902 | 108.6131 | 0.55177 | 175 | 7.1455 | 7.2145 | 7.3282 | 7.4802 | 7.1856 | 106.0905 | 5.6921 | 179997 | 89.564 | 0.16024 | 0.22382 | 179996.5 | 0 | 0 | 0.5 | 101.4579 | 0.029482 | 0.012 | 176292.5 | 0.15794 | 0.22786 | 3704.5 | 0.26966 | 89.564 | 115.6292 | 0.89147 | 0
Image_H100_ModelSize_128 | 106.7189 | 141.0667 | 40 | 78.5131 | 101.7192 | 130.6145 | 40 | 76.0659 | 100.6432 | 75.9738 | 180000.5 | 101.0667 | 0.7472 | 1.4562 | 179768 | 232 | 0 | 0.5 | 106.7385 | 0.031755 | 0.013 | 179049 | 0.73468 | 1.5034 | 951.5 | 3.1041 | 101.0667 | 105.8221 | 4.1802 | 232 | 9.0547 | 9.1082 | 9.5336 | 9.661 | 9.1554 | 108.6635 | 8.414 | 180000 | 90.6145 | 0.16089 | 0.30872 | 179999.5 | 0 | 0 | 0.5 | 101.7203 | 0.030924 | 0.012 | 179197.5 | 0.15882 | 0.31856 | 802.5 | 0.62377 | 90.6145 | 106.6731 | 4.6047 | 0
Image_H100_ModelSize_256 | 107.5488 | 143.6624 | 40 | 81.2155 | 102.4782 | 132.0866 | 40 | 77.1454 | 101.393 | 77.3829 | 179997.5 | 103.6624 | 0.75805 | 1.6365 | 179870 | 0 | 127 | 0.5 | 107.569 | 0.032703 | 0.013 | 178483 | 0.74445 | 1.6956 | 1514.5 | 2.3611 | 103.6624 | 112.6473 | 2.7053 | 127 | 11.4739 | 11.5379 | 11.8003 | 11.878 | 11.5155 | 109.973 | 16.0853 | 180000 | 92.0866 | 0.16239 | 0.34498 | 179999.5 | 0 | 0 | 0.5 | 102.4794 | 0.031588 | 0.012 | 179574.5 | 0.16081 | 0.35229 | 425.5 | 0.82985 | 92.0866 | 105.922 | 8.9894 | 0
Image_H100_ModelSize_512 | 108.3836 | 147.3183 | 40 | 84.455 | 103.2503 | 133.922 | 40 | 77.1941 | 102.1567 | 76.6875 | 180000.5 | 107.3183 | 0.7676 | 1.8807 | 179956 | 0 | 44 | 0.5 | 108.4046 | 0.03358 | 0.013 | 177867 | 0.75098 | 1.9018 | 2133.5 | 2.1533 | 107.3183 | 115.001 | 2.1062 | 44 | 14.3471 | 14.5905 | 15.2697 | 15.4902 | 14.6088 | 111.3666 | 48.7452 | 180000 | 93.922 | 0.16372 | 0.39419 | 179999.5 | 0 | 0 | 0.5 | 103.2515 | 0.032003 | 0.012 | 179664.5 | 0.16251 | 0.40659 | 335.5 | 0.80848 | 93.922 | 113.0114 | 11.7236 | 0
Text_B200_BatchSize16 | 106.4106 | 136.6417 | 40 | 75.7643 | 101.4811 | 129.8087 | 40 | 75.5174 | 100.4135 | 75.5253 | 180000.5 | 96.6417 | 0.73636 | 0.96368 | 179604.5 | 395.5 | 0 | 0.5 | 106.4295 | 0.034915 | 0.013 | 177233.5 | 0.72016 | 1.009 | 2767 | 1.7746 | 96.6417 | 106.9768 | 1.6164 | 395.5 | 6.2399 | 6.2304 | 6.4616 | 9.01 | 6.5018 | 104.93 | 4.7097 | 180000 | 89.8087 | 0.15939 | 0.20764 | 179999.5 | 0 | 0 | 0.5 | 101.4822 | 0.032615 | 0.012 | 177337 | 0.1564 | 0.21668 | 2663 | 0.3584 | 89.8087 | 102.4727 | 1.4975 | 0
Text_B200_BatchSize2 | 105.4423 | 133.6085 | 40 | 74.3854 | 100.5494 | 127.9134 | 40 | 74.3076 | 99.4875 | 74.0386 | 180000.5 | 93.6085 | 0.73089 | 0.79873 | 180000 | 0 | 0 | 0.5 | 105.4608 | 0.035974 | 0.013 | 177455 | 0.72699 | 0.83365 | 2545.5 | 1.0024 | 93.6085 | 105.9967 | 1.7677 | 0 | [7 empty] | 180000 | 87.9134 | 0.15863 | 0.17291 | 179999.5 | 0 | 0 | 0.5 | 100.5505 | 0.029079 | 0.012 | 178004.5 | 0.15788 | 0.18041 | 1995.5 | 0.22612 | 87.9134 | 106.9085 | 1.5761 | 0
Text_B200_BatchSize32 | 105.7249 | 135.0776 | 40 | 75.482 | 100.8093 | 128.4771 | 40 | 74.9778 | 99.7445 | 74.8672 | 180000.5 | 95.0776 | 0.73433 | 0.90768 | 179600.5 | 399.5 | 0 | 0.5 | 105.7436 | 0.036192 | 0.013 | 177512 | 0.71704 | 0.94377 | 2488.5 | 1.9676 | 95.0776 | 106.5391 | 1.8892 | 399.5 | 5.9092 | 5.9176 | 6.1189 | 6.2919 | 5.9301 | 104.5003 | 4.6216 | 180000 | 88.4771 | 0.15911 | 0.19603 | 179999.5 | 0 | 0 | 0.5 | 100.8104 | 0.032314 | 0.012 | 177563.5 | 0.15596 | 0.20397 | 2436.5 | 0.38892 | 88.4771 | 102.4097 | 1.6191 | 0
Text_B200_Deepspeedds_z1 | 106.7826 | 138.1682 | 40 | 75.6259 | 101.8393 | 130.557 | 40 | 75.4466 | 100.7696 | 75.4675 | 180000.5 | 98.1682 | 0.73849 | 1.062 | 179589 | 409.5 | 1.5 | 0.5 | 106.8016 | 0.034754 | 0.013 | 177906 | 0.71503 | 1.1106 | 2094.5 | 2.7314 | 98.1682 | 106.8961 | 2.1816 | 411 | 7.1868 | 7.1731 | 7.3285 | 11.0291 | 7.6968 | 105.5862 | 4.3902 | 180000 | 90.557 | 0.15969 | 0.22916 | 179999.5 | 0 | 0 | 0.5 | 101.8404 | 0.033343 | 0.012 | 177904.5 | 0.15539 | 0.23909 | 2095.5 | 0.52435 | 90.557 | 101.1949 | 2.0255 | 0
Text_B200_Deepspeedds_z2 | 106.3301 | 136.5661 | 40 | 75.8455 | 101.399 | 129.6663 | 40 | 75.4925 | 100.3314 | 75.4739 | 180000.5 | 96.5661 | 0.73662 | 0.97319 | 179600.5 | 399.5 | 0 | 0.5 | 106.349 | 0.035042 | 0.013 | 177267.5 | 0.71995 | 1.0289 | 2733 | 1.8176 | 96.5661 | 106.7223 | 1.6372 | 399.5 | 6.319 | 6.3093 | 6.5659 | 8.6213 | 6.4676 | 105.0061 | 4.6765 | 180000 | 89.6663 | 0.15943 | 0.20968 | 179999.5 | 0 | 0 | 0.5 | 101.4001 | 0.033062 | 0.012 | 177371 | 0.15636 | 0.22051 | 2629 | 0.36621 | 89.6663 | 102.1927 | 1.5394 | 0
Text_B200_Deepspeedds_z3 | 106.4106 | 136.6417 | 40 | 75.7643 | 101.4811 | 129.8087 | 40 | 75.5174 | 100.4135 | 75.5253 | 180000.5 | 96.6417 | 0.73636 | 0.96368 | 179604.5 | 395.5 | 0 | 0.5 | 106.4295 | 0.034915 | 0.013 | 177233.5 | 0.72016 | 1.009 | 2767 | 1.7746 | 96.6417 | 106.9768 | 1.6164 | 395.5 | 6.2399 | 6.2304 | 6.4616 | 9.01 | 6.5018 | 104.93 | 4.7097 | 180000 | 89.8087 | 0.15939 | 0.20764 | 179999.5 | 0 | 0 | 0.5 | 101.4822 | 0.032615 | 0.012 | 177337 | 0.1564 | 0.21668 | 2663 | 0.3584 | 89.8087 | 102.4727 | 1.4975 | 0
Text_B200_Lamma_1B | 106.0344 | 137.4472 | 40 | 76.2947 | 101.0927 | 129.262 | 40 | 75.3571 | 100.0244 | 75.2194 | 180000.5 | 97.4472 | 0.73832 | 1.162 | 179208.5 | 791.5 | 0 | 0.5 | 106.0535 | 0.031659 | 0.013 | 178977 | 0.71011 | 1.2057 | 1023.5 | 5.6717 | 97.4472 | 106.9582 | 3.8952 | 791.5 | 6.9151 | 6.9455 | 7.1514 | 7.3697 | 6.9458 | 106.3885 | 2.7026 | 180000 | 89.262 | 0.15966 | 0.24906 | 179999.5 | 0 | 0 | 0.5 | 101.0939 | 0.030927 | 0.012 | 179020.5 | 0.15464 | 0.25852 | 979.5 | 1.0786 | 89.262 | 102.5691 | 3.8734 | 0
Text_B200_Lamma_3B | 106.2761 | 136.7864 | 40 | 76.2097 | 101.3253 | 128.9645 | 40 | 74.9553 | 100.2556 | 74.9049 | 180000.5 | 96.7864 | 0.73971 | 1.1079 | 179485 | 515 | 0 | 0.5 | 106.2953 | 0.033283 | 0.013 | 178246 | 0.71844 | 1.1765 | 1754.5 | 2.9013 | 96.7864 | 107.969 | 2.4244 | 515 | 7.0513 | 7.0502 | 7.3256 | 8.3433 | 7.0894 | 105.9652 | 4.1418 | 180000 | 88.9645 | 0.15986 | 0.23769 | 179999.5 | 0 | 0 | 0.5 | 101.3264 | 0.031828 | 0.012 | 178302.5 | 0.15604 | 0.25128 | 1697.5 | 0.56072 | 88.9645 | 102.2639 | 2.2983 | 0
Text_B200_Lamma_8B | 106.4106 | 136.6417 | 40 | 75.7643 | 101.4811 | 129.8087 | 40 | 75.5174 | 100.4135 | 75.5253 | 180000.5 | 96.6417 | 0.73636 | 0.96368 | 179604.5 | 395.5 | 0 | 0.5 | 106.4295 | 0.034915 | 0.013 | 177233.5 | 0.72016 | 1.009 | 2767 | 1.7746 | 96.6417 | 106.9768 | 1.6164 | 395.5 | 6.2399 | 6.2304 | 6.4616 | 9.01 | 6.5018 | 104.93 | 4.7097 | 180000 | 89.8087 | 0.15939 | 0.20764 | 179999.5 | 0 | 0 | 0.5 | 101.4822 | 0.032615 | 0.012 | 177337 | 0.1564 | 0.21668 | 2663 | 0.3584 | 89.8087 | 102.4727 | 1.4975 | 0
Text_B200_SeqLength_1024 | 106.2107 | 136.2444 | 40 | 75.8594 | 101.2818 | 129.419 | 40 | 75.4095 | 100.2146 | 75.4286 | 180000.5 | 96.2444 | 0.7363 | 0.96378 | 179604.5 | 395.5 | 0 | 0.5 | 106.2296 | 0.035209 | 0.013 | 177216.5 | 0.71992 | 1.0131 | 2784 | 1.7785 | 96.2444 | 106.8269 | 1.6283 | 395.5 | 6.2836 | 6.2699 | 6.52 | 8.112 | 6.3656 | 104.9385 | 4.7857 | 180000 | 89.419 | 0.15938 | 0.20771 | 179999.5 | 0 | 0 | 0.5 | 101.2829 | 0.03305 | 0.012 | 177283 | 0.15637 | 0.21819 | 2717 | 0.35628 | 89.419 | 102.5158 | 1.4971 | 0
Text_B200_SeqLength_2048 | 106.4106 | 136.6417 | 40 | 75.7643 | 101.4811 | 129.8087 | 40 | 75.5174 | 100.4135 | 75.5253 | 180000.5 | 96.6417 | 0.73636 | 0.96368 | 179604.5 | 395.5 | 0 | 0.5 | 106.4295 | 0.034915 | 0.013 | 177233.5 | 0.72016 | 1.009 | 2767 | 1.7746 | 96.6417 | 106.9768 | 1.6164 | 395.5 | 6.2399 | 6.2304 | 6.4616 | 9.01 | 6.5018 | 104.93 | 4.7097 | 180000 | 89.8087 | 0.15939 | 0.20764 | 179999.5 | 0 | 0 | 0.5 | 101.4822 | 0.032615 | 0.012 | 177337 | 0.1564 | 0.21668 | 2663 | 0.3584 | 89.8087 | 102.4727 | 1.4975 | 0
Text_B200_SeqLength_4096 | 106.2538 | 136.3974 | 40 | 75.8472 | 101.3246 | 129.537 | 40 | 75.4456 | 100.2574 | 75.4023 | 180000.5 | 96.3974 | 0.73633 | 0.96388 | 179604.5 | 395.5 | 0 | 0.5 | 106.2727 | 0.034957 | 0.013 | 177231.5 | 0.72004 | 1.0016 | 2769 | 1.7793 | 96.3974 | 107.1509 | 1.6201 | 395.5 | 6.2723 | 6.2532 | 6.5007 | 8.3645 | 6.3794 | 104.937 | 4.7193 | 180000 | 89.537 | 0.15939 | 0.2077 | 179999.5 | 0 | 0 | 0.5 | 101.3257 | 0.032705 | 0.012 | 177319 | 0.15639 | 0.21558 | 2681 | 0.35774 | 89.537 | 102.5533 | 1.4929 | 0
Text_H100_BatchSize16 | 105.6901 | 134.7301 | 40 | 75.413 | 100.7771 | 128.3306 | 40 | 74.9528 | 99.7125 | 74.7465 | 180000.5 | 94.7301 | 0.73397 | 0.89112 | 179732 | 268 | 0 | 0.5 | 105.7088 | 0.037311 | 0.013 | 177095.5 | 0.71924 | 0.93738 | 2905 | 1.6322 | 94.7301 | 106.2588 | 1.6913 | 268 | 6.0736 | 6.0899 | 6.3084 | 6.424 | 6.1022 | 104.255 | 6.1702 | 180000 | 88.3306 | 0.15906 | 0.19251 | 179999.5 | 0 | 0 | 0.5 | 100.7782 | 0.032754 | 0.012 | 177073 | 0.15635 | 0.20234 | 2927 | 0.32309 | 88.3306 | 101.2711 | 1.3756 | 0
Text_H100_BatchSize2 | 105.6216 | 133.4617 | 40 | 74.263 | 100.726 | 127.5906 | 40 | 74.067 | 99.6635 | 74.0481 | 180000.5 | 93.4617 | 0.73128 | 0.81888 | 179997 | 3 | 0 | 0.5 | 105.6401 | 0.036869 | 0.013 | 176921.5 | 0.72619 | 0.87976 | 3079 | 1.0239 | 93.4617 | 105.6071 | 1.5365 | 3 | 5.4903 | 5.569 | 5.8801 | 5.8801 | 5.6235 | 119.3969 | 55.9797 | 180000 | 87.5906 | 0.15869 | 0.17724 | 179999.5 | 0 | 0 | 0.5 | 100.7271 | 0.030941 | 0.012 | 177154 | 0.15771 | 0.19078 | 2846 | 0.21983 | 87.5906 | 103.5582 | 1.2535 | 0
Text_H100_BatchSize32 | 105.6397 | 134.7673 | 40 | 75.4523 | 100.7297 | 128.3307 | 40 | 74.9516 | 99.6656 | 74.8182 | 180000.5 | 94.7673 | 0.7335 | 0.8773 | 179749 | 251 | 0 | 0.5 | 105.6584 | 0.038761 | 0.013 | 177511 | 0.71958 | 0.91453 | 2489.5 | 1.7265 | 94.7673 | 106.3771 | 2.0555 | 251 | 6.0218 | 6.0361 | 6.2429 | 6.3184 | 6.0427 | 104.2889 | 6.6494 | 180000 | 88.3307 | 0.159 | 0.18959 | 179999.5 | 0 | 0 | 0.5 | 100.7309 | 0.032169 | 0.012 | 177596.5 | 0.15642 | 0.19771 | 2403.5 | 0.34907 | 88.3307 | 101.0866 | 1.6329 | 0
Text_H100_Deepspeedds_z1 | 106.0335 | 136.2177 | 40 | 75.9689 | 101.0961 | 128.846 | 40 | 75.2037 | 100.0283 | 75.081 | 180000.5 | 96.2177 | 0.73767 | 1.0471 | 179719 | 281 | 0 | 0.5 | 106.0524 | 0.033801 | 0.013 | 178616 | 0.71086 | 1.0607 | 1384.5 | 4.1958 | 96.2177 | 106.5082 | 3.1331 | 281 | 7.2907 | 7.3464 | 7.4517 | 7.4966 | 7.3295 | 105.0855 | 5.0006 | 180000 | 88.846 | 0.15957 | 0.22504 | 179999.5 | 0 | 0 | 0.5 | 101.0972 | 0.03317 | 0.012 | 178612.5 | 0.15471 | 0.22816 | 1387.5 | 0.78575 | 88.846 | 101.0522 | 3.0156 | 0
Text_H100_Deepspeedds_z2 | 105.7233 | 134.8646 | 40 | 75.466 | 100.8082 | 128.3955 | 40 | 74.909 | 99.7434 | 74.876 | 180000.5 | 94.8646 | 0.73425 | 0.90406 | 179721.5 | 278.5 | 0 | 0.5 | 105.742 | 0.037523 | 0.013 | 176894.5 | 0.7181 | 0.97727 | 3106 | 1.6542 | 94.8646 | 106.4468 | 1.5963 | 278.5 | 6.1521 | 6.1863 | 6.4508 | 6.5538 | 6.1992 | 104.5439 | 6.1964 | 180000 | 88.3955 | 0.1591 | 0.19528 | 179999.5 | 0 | 0 | 0.5 | 100.8093 | 0.033447 | 0.012 | 176892 | 0.15613 | 0.20711 | 3108 | 0.32797 | 88.3955 | 101.1644 | 1.3366 | 0
Text_H100_Deepspeedds_z3 | 105.6901 | 134.7301 | 40 | 75.413 | 100.7771 | 128.3306 | 40 | 74.9528 | 99.7125 | 74.7465 | 180000.5 | 94.7301 | 0.73397 | 0.89112 | 179732 | 268 | 0 | 0.5 | 105.7088 | 0.037311 | 0.013 | 177095.5 | 0.71924 | 0.93738 | 2905 | 1.6322 | 94.7301 | 106.2588 | 1.6913 | 268 | 6.0736 | 6.0899 | 6.3084 | 6.424 | 6.1022 | 104.255 | 6.1702 | 180000 | 88.3306 | 0.15906 | 0.19251 | 179999.5 | 0 | 0 | 0.5 | 100.7782 | 0.032754 | 0.012 | 177073 | 0.15635 | 0.20234 | 2927 | 0.32309 | 88.3306 | 101.2711 | 1.3756 | 0
Text_H100_Lamma_1B | 106.3654 | 138.2622 | 40 | 76.862 | 101.3986 | 129.6668 | 40 | 75.3885 | 100.327 | 75.338 | 180000.5 | 98.2622 | 0.74215 | 1.2313 | 179289 | 711 | 0 | 0.5 | 106.3847 | 0.031859 | 0.013 | 178780 | 0.7108 | 1.2985 | 1220.5 | 5.3355 | 98.2622 | 108.0861 | 3.2885 | 711 | 8.1963 | 8.2075 | 8.4493 | 8.945 | 8.2204 | 106.6402 | 2.9894 | 180000 | 89.6668 | 0.16019 | 0.26333 | 179999.5 | 0 | 0 | 0.5 | 101.3998 | 0.031327 | 0.012 | 178813.5 | 0.15458 | 0.27517 | 1186.5 | 1.0063 | 89.6668 | 102.9954 | 3.2546 | 0
Text_H100_Lamma_3B | 106.1997 | 136.2705 | 40 | 76.1011 | 101.2568 | 128.9297 | 40 | 75.3 | 100.1881 | 75.3141 | 180000.5 | 96.2705 | 0.7385 | 1.0253 | 179573 | 427 | 0 | 0.5 | 106.2188 | 0.034455 | 0.013 | 177431 | 0.71941 | 1.0764 | 2569.5 | 2.0568 | 96.2705 | 107.5424 | 1.712 | 427 | 6.9727 | 6.9724 | 7.221 | 8.0265 | 7.0031 | 105.3293 | 4.607 | 180000 | 88.9297 | 0.15969 | 0.22047 | 179999.5 | 0 | 0 | 0.5 | 101.258 | 0.03267 | 0.012 | 177521.5 | 0.15622 | 0.23268 | 2478.5 | 0.40817 | 88.9297 | 102.3246 | 1.6148 | 0
Text_H100_Lamma_8B | 105.6901 | 134.7301 | 40 | 75.413 | 100.7771 | 128.3306 | 40 | 74.9528 | 99.7125 | 74.7465 | 180000.5 | 94.7301 | 0.73397 | 0.89112 | 179732 | 268 | 0 | 0.5 | 105.7088 | 0.037311 | 0.013 | 177095.5 | 0.71924 | 0.93738 | 2905 | 1.6322 | 94.7301 | 106.2588 | 1.6913 | 268 | 6.0736 | 6.0899 | 6.3084 | 6.424 | 6.1022 | 104.255 | 6.1702 | 180000 | 88.3306 | 0.15906 | 0.19251 | 179999.5 | 0 | 0 | 0.5 | 100.7782 | 0.032754 | 0.012 | 177073 | 0.15635 | 0.20234 | 2927 | 0.32309 | 88.3306 | 101.2711 | 1.3756 | 0
Text_H100_SeqLength_1024 | 105.6888 | 134.7652 | 40 | 75.5204 | 100.776 | 128.3738 | 40 | 75.1389 | 99.7115 | 74.99 | 180000.5 | 94.7652 | 0.73392 | 0.89106 | 179728 | 272 | 0 | 0.5 | 105.7075 | 0.037258 | 0.013 | 177102 | 0.71897 | 0.94049 | 2898.5 | 1.6478 | 94.7652 | 105.9474 | 1.6926 | 272 | 6.0631 | 6.0809 | 6.3077 | 6.4292 | 6.0934 | 104.2984 | 6.0971 | 180000 | 88.3738 | 0.15905 | 0.1925 | 179999.5 | 0 | 0 | 0.5 | 100.7771 | 0.032828 | 0.012 | 177106.5 | 0.15631 | 0.20303 | 2893.5 | 0.32711 | 88.3738 | 101.4652 | 1.3971 | 0
Text_H100_SeqLength_2048 | 105.6901 | 134.7301 | 40 | 75.413 | 100.7771 | 128.3306 | 40 | 74.9528 | 99.7125 | 74.7465 | 180000.5 | 94.7301 | 0.73397 | 0.89112 | 179732 | 268 | 0 | 0.5 | 105.7088 | 0.037311 | 0.013 | 177095.5 | 0.71924 | 0.93738 | 2905 | 1.6322 | 94.7301 | 106.2588 | 1.6913 | 268 | 6.0736 | 6.0899 | 6.3084 | 6.424 | 6.1022 | 104.255 | 6.1702 | 180000 | 88.3306 | 0.15906 | 0.19251 | 179999.5 | 0 | 0 | 0.5 | 100.7782 | 0.032754 | 0.012 | 177073 | 0.15635 | 0.20234 | 2927 | 0.32309 | 88.3306 | 101.2711 | 1.3756 | 0
Text_H100_SeqLength_4096 | 105.6983 | 134.765 | 40 | 75.4479 | 100.7848 | 128.3566 | 40 | 74.9999 | 99.7202 | 74.8206 | 180000.5 | 94.765 | 0.73403 | 0.89338 | 179732 | 268 | 0 | 0.5 | 105.717 | 0.037199 | 0.013 | 177122.5 | 0.71908 | 0.94071 | 2878 | 1.6542 | 94.765 | 106.086 | 1.7013 | 268 | 6.0927 | 6.1022 | 6.3314 | 6.4255 | 6.1197 | 104.2851 | 6.1357 | 180000 | 88.3566 | 0.15907 | 0.19299 | 179999.5 | 0 | 0 | 0.5 | 100.7859 | 0.032863 | 0.012 | 177100 | 0.15632 | 0.20308 | 2900 | 0.32702 | 88.3566 | 101.6835 | 1.3958 | 0

## Nf_results
scenario | Mission_duration_s | IGBT_Nf_eq | IGBT_Nf_eq_dT_ge10 | IGBT_Nf_eq_dT_lt10 | IGBT_Nf_eq_load_cycles | IGBT_Nf_eq_grid_cycles | IGBT_Nf_worst_cycle | IGBT_worst_cycle_dT_K | IGBT_worst_cycle_Tmean_C | Diode_Nf_eq | Diode_Nf_eq_dT_ge10 | Diode_Nf_eq_dT_lt10 | Diode_Nf_eq_load_cycles | Diode_Nf_eq_grid_cycles | Diode_Nf_worst_cycle | Diode_worst_cycle_dT_K | Diode_worst_cycle_Tmean_C | Limiting_device | IGBT_lifetime_years_actual | Diode_lifetime_years_actual
Image_B200_BatchSize_128 | 3600 | 70847.713 | inf | 70847.713 | 70847.713 | 7.8377e+24 | 35423.8598 | 100.1928 | 90.0964 | 62720.1022 | inf | 62720.1022 | 62720.1022 | 3.9682e+35 | 31360.0511 | 90.188 | 85.094 | Diode | 8.0876 | 7.1598
Image_B200_BatchSize_256 | 3600 | 63013.0231 | inf | 63013.0231 | 63013.0231 | 7.4726e+23 | 31506.5876 | 102.3546 | 91.1773 | 60581.6307 | inf | 60581.6307 | 60581.6307 | 5.3596e+34 | 30290.8154 | 90.7705 | 85.3853 | Diode | 7.1933 | 6.9157
Image_B200_BatchSize_512 | 3600 | 57801.2511 | inf | 57801.2511 | 57801.2511 | 1.9813e+23 | 28901.0663 | 103.971 | 91.9855 | 59100.0342 | inf | 59100.0342 | 59100.0342 | 1.7521e+34 | 29550.0171 | 91.1883 | 85.5942 | IGBT | 6.5983 | 6.7466
Image_B200_ImageSize_128 | 3600 | 99593.2749 | inf | 99593.2749 | 99593.2749 | 2.9466e+28 | 49796.6374 | 94.1233 | 87.0617 | 70553.4738 | inf | 70553.4738 | 70553.4738 | 4.9176e+38 | 35276.7369 | 88.2355 | 84.1177 | Diode | 11.3691 | 8.054
Image_B200_ImageSize_32 | 3600 | 70847.713 | inf | 70847.713 | 70847.713 | 7.8377e+24 | 35423.8598 | 100.1928 | 90.0964 | 62720.1022 | inf | 62720.1022 | 62720.1022 | 3.9682e+35 | 31360.0511 | 90.188 | 85.094 | Diode | 8.0876 | 7.1598
Image_B200_ImageSize_64 | 3600 | 80169.1372 | inf | 80169.1372 | 80169.1372 | 1.4057e+26 | 40084.5689 | 97.9535 | 88.9768 | 63992.9835 | inf | 63992.9835 | 63992.9835 | 4.5082e+36 | 31996.4918 | 89.852 | 84.926 | Diode | 9.1517 | 7.3051
Image_B200_ModelSize_128 | 3600 | 70847.713 | inf | 70847.713 | 70847.713 | 7.8377e+24 | 35423.8598 | 100.1928 | 90.0964 | 62720.1022 | inf | 62720.1022 | 62720.1022 | 3.9682e+35 | 31360.0511 | 90.188 | 85.094 | Diode | 8.0876 | 7.1598
Image_B200_ModelSize_256 | 3600 | 61347.3122 | inf | 61347.3122 | 61347.3122 | 5.5024e+23 | 30673.7407 | 102.8541 | 91.4271 | 58579.2766 | inf | 58579.2766 | 58579.2766 | 3.9736e+34 | 29289.6383 | 91.338 | 85.669 | Diode | 7.0031 | 6.6871
Image_B200_ModelSize_512 | 3600 | 50262.747 | inf | 50262.747 | 50262.747 | 6.3448e+22 | 25132.0972 | 106.6319 | 93.3159 | 52200.4648 | inf | 52200.4648 | 52200.4648 | 4.8129e+33 | 26100.2324 | 93.3076 | 86.6538 | IGBT | 5.7378 | 5.959
Image_H100_BatchSize_128 | 3600 | 67553.1837 | inf | 67553.1837 | 67553.1837 | 4.9142e+24 | 33776.5998 | 101.0667 | 90.5333 | 61146.4457 | inf | 61146.4457 | 61146.4457 | 2.5741e+35 | 30573.2228 | 90.6145 | 85.3072 | Diode | 7.7116 | 6.9802
Image_H100_BatchSize_256 | 3600 | 83161.7975 | inf | 83161.7975 | 83161.7975 | 2.1383e+26 | 41580.8988 | 97.2976 | 88.6488 | 66149.9871 | inf | 66149.9871 | 66149.9871 | 6.3578e+36 | 33074.9936 | 89.3 | 84.65 | Diode | 9.4934 | 7.5514
Image_H100_BatchSize_512 | 3600 | 51210.2427 | inf | 51210.2427 | 51210.2427 | 5.1855e+22 | 25606.6413 | 106.2724 | 93.1362 | 55238.6259 | inf | 55238.6259 | 55238.6259 | 5.0771e+33 | 27619.3129 | 92.3367 | 86.1684 | IGBT | 5.8459 | 6.3058
Image_H100_ImageSize_16 | 3600 | 79848.5959 | inf | 79848.5959 | 79848.5959 | 9.6402e+25 | 39924.298 | 98.0255 | 89.0127 | 65999.4392 | inf | 65999.4392 | 65999.4392 | 3.4394e+36 | 32999.7196 | 89.3379 | 84.669 | Diode | 9.1151 | 7.5342
Image_H100_ImageSize_32 | 3600 | 67553.1837 | inf | 67553.1837 | 67553.1837 | 4.9142e+24 | 33776.5998 | 101.0667 | 90.5333 | 61146.4457 | inf | 61146.4457 | 61146.4457 | 2.5741e+35 | 30573.2228 | 90.6145 | 85.3072 | Diode | 7.7116 | 6.9802
Image_H100_ImageSize_64 | 3600 | 85028.795 | inf | 85028.795 | 85028.795 | 7.3448e+26 | 42514.3977 | 96.902 | 88.451 | 65108.1052 | inf | 65108.1052 | 65108.1052 | 1.6507e+37 | 32554.0526 | 89.564 | 84.782 | Diode | 9.7065 | 7.4324
Image_H100_ModelSize_128 | 3600 | 67553.1837 | inf | 67553.1837 | 67553.1837 | 4.9142e+24 | 33776.5998 | 101.0667 | 90.5333 | 61146.4457 | inf | 61146.4457 | 61146.4457 | 2.5741e+35 | 30573.2228 | 90.6145 | 85.3072 | Diode | 7.7116 | 6.9802
Image_H100_ModelSize_256 | 3600 | 58757.7116 | inf | 58757.7116 | 58757.7116 | 4.7814e+23 | 29379.0042 | 103.6624 | 91.8312 | 56054.7124 | inf | 56054.7124 | 56054.7124 | 3.3855e+34 | 28027.3562 | 92.0866 | 86.0433 | Diode | 6.7075 | 6.3989
Image_H100_ModelSize_512 | 3600 | 48505.1797 | inf | 48505.1797 | 48505.1797 | 5.4247e+22 | 24254.0559 | 107.3183 | 93.6592 | 50378.978 | inf | 50378.978 | 50378.978 | 4.1214e+33 | 25189.489 | 93.922 | 86.961 | IGBT | 5.5371 | 5.751
Text_B200_BatchSize16 | 3600 | 86286.4847 | inf | 86286.4847 | 86286.4847 | 3.6932e+27 | 43143.2425 | 96.6417 | 88.3208 | 64160.9332 | inf | 64160.9332 | 64160.9332 | 7.8777e+37 | 32080.4666 | 89.8087 | 84.9044 | Diode | 9.8501 | 7.3243
Text_B200_BatchSize2 | 3600 | 102596.4089 | inf | 102596.4089 | 102596.4089 | 5.0535e+28 | 51298.2045 | 93.6085 | 86.8043 | 71950.7822 | inf | 71950.7822 | 71950.7822 | 7.8269e+38 | 35975.3911 | 87.9134 | 83.9567 | Diode | 11.7119 | 8.2136
Text_B200_BatchSize32 | 3600 | 94288.0721 | inf | 94288.0721 | 94288.0721 | 9.6669e+27 | 47144.0361 | 95.0776 | 87.5388 | 69524.4861 | inf | 69524.4861 | 69524.4861 | 1.8377e+38 | 34762.243 | 88.4771 | 84.2385 | Diode | 10.7635 | 7.9366
Text_B200_Deepspeedds_z1 | 3600 | 79220.6883 | inf | 79220.6883 | 79220.6883 | 1.2822e+27 | 39610.3459 | 98.1682 | 89.0841 | 61358.7327 | inf | 61358.7327 | 61358.7327 | 3.1226e+37 | 30679.3663 | 90.557 | 85.2785 | Diode | 9.0435 | 7.0044
Text_B200_Deepspeedds_z2 | 3600 | 86653.5847 | inf | 86653.5847 | 86653.5847 | 3.1819e+27 | 43326.7924 | 96.5661 | 88.283 | 64710.9594 | inf | 64710.9594 | 64710.9594 | 6.895e+37 | 32355.4797 | 89.6663 | 84.8331 | Diode | 9.892 | 7.3871
Text_B200_Deepspeedds_z3 | 3600 | 86286.4847 | inf | 86286.4847 | 86286.4847 | 3.6932e+27 | 43143.2425 | 96.6417 | 88.3208 | 64160.9332 | inf | 64160.9332 | 64160.9332 | 7.8777e+37 | 32080.4666 | 89.8087 | 84.9044 | Diode | 9.8501 | 7.3243
Text_B200_Lamma_1B | 3600 | 82467.6232 | inf | 82467.6232 | 82467.6232 | 2.6931e+26 | 41233.8119 | 97.4472 | 88.7236 | 66301.7614 | inf | 66301.7614 | 66301.7614 | 8.3724e+36 | 33150.8807 | 89.262 | 84.631 | Diode | 9.4141 | 7.5687
Text_B200_Lamma_3B | 3600 | 85583.1774 | inf | 85583.1774 | 85583.1774 | 4.3598e+26 | 42791.589 | 96.7864 | 88.3932 | 67502.4124 | inf | 67502.4124 | 67502.4124 | 1.2174e+37 | 33751.2062 | 88.9645 | 84.4822 | Diode | 9.7698 | 7.7058
Text_B200_Lamma_8B | 3600 | 86286.4847 | inf | 86286.4847 | 86286.4847 | 3.6932e+27 | 43143.2425 | 96.6417 | 88.3208 | 64160.9332 | inf | 64160.9332 | 64160.9332 | 7.8777e+37 | 32080.4666 | 89.8087 | 84.9044 | Diode | 9.8501 | 7.3243
Text_B200_SeqLength_1024 | 3600 | 88241.1727 | inf | 88241.1727 | 88241.1727 | 3.7368e+27 | 44120.5864 | 96.2444 | 88.1222 | 65679.0901 | inf | 65679.0901 | 65679.0901 | 7.9255e+37 | 32839.545 | 89.419 | 84.7095 | Diode | 10.0732 | 7.4976
Text_B200_SeqLength_2048 | 3600 | 86286.4847 | inf | 86286.4847 | 86286.4847 | 3.6932e+27 | 43143.2425 | 96.6417 | 88.3208 | 64160.9332 | inf | 64160.9332 | 64160.9332 | 7.8777e+37 | 32080.4666 | 89.8087 | 84.9044 | Diode | 9.8501 | 7.3243
Text_B200_SeqLength_4096 | 3600 | 87482.6882 | inf | 87482.6882 | 87482.6882 | 3.7281e+27 | 43741.3441 | 96.3974 | 88.1987 | 65214.8882 | inf | 65214.8882 | 65214.8882 | 7.9211e+37 | 32607.4441 | 89.537 | 84.7685 | Diode | 9.9866 | 7.4446
Text_H100_BatchSize16 | 3600 | 96181.2709 | inf | 96181.2709 | 96181.2709 | 1.3646e+28 | 48090.6355 | 94.7301 | 87.365 | 70145.6149 | inf | 70145.6149 | 70145.6149 | 2.4998e+38 | 35072.8075 | 88.3306 | 84.1653 | Diode | 10.9796 | 8.0075
Text_H100_BatchSize2 | 3600 | 103472.0952 | inf | 103472.0952 | 103472.0952 | 4.3246e+28 | 51736.0476 | 93.4617 | 86.7309 | 73384.8099 | inf | 73384.8099 | 73384.8099 | 6.9034e+38 | 36692.405 | 87.5906 | 83.7953 | Diode | 11.8119 | 8.3773
Text_H100_BatchSize32 | 3600 | 95975.9992 | inf | 95975.9992 | 95975.9992 | 1.6822e+28 | 47987.9996 | 94.7673 | 87.3837 | 70145.1745 | inf | 70145.1745 | 70145.1745 | 3.0809e+38 | 35072.5873 | 88.3307 | 84.1654 | Diode | 10.9562 | 8.0074
Text_H100_Deepspeedds_z1 | 3600 | 88373.2891 | inf | 88373.2891 | 88373.2891 | 1.3245e+27 | 44186.6448 | 96.2177 | 88.1088 | 67987.6074 | inf | 67987.6074 | 67987.6074 | 3.3382e+37 | 33993.8037 | 88.846 | 84.423 | Diode | 10.0883 | 7.7611
Text_H100_Deepspeedds_z2 | 3600 | 95443.379 | inf | 95443.379 | 95443.379 | 1.1662e+28 | 47721.6895 | 94.8646 | 87.4323 | 69869.4256 | inf | 69869.4256 | 69869.4256 | 2.1741e+38 | 34934.7128 | 88.3955 | 84.1978 | Diode | 10.8954 | 7.976
Text_H100_Deepspeedds_z3 | 3600 | 96181.2709 | inf | 96181.2709 | 96181.2709 | 1.3646e+28 | 48090.6355 | 94.7301 | 87.365 | 70145.6149 | inf | 70145.6149 | 70145.6149 | 2.4998e+38 | 35072.8075 | 88.3306 | 84.1653 | Diode | 10.9796 | 8.0075
Text_H100_Lamma_1B | 3600 | 78804.133 | inf | 78804.133 | 78804.133 | 8.9893e+25 | 39402.0705 | 98.2622 | 89.1311 | 64707.4012 | inf | 64707.4012 | 64707.4012 | 3.1467e+36 | 32353.7006 | 89.6668 | 84.8334 | Diode | 8.9959 | 7.3867
Text_H100_Lamma_3B | 3600 | 88114.0389 | inf | 88114.0389 | 88114.0389 | 1.3863e+27 | 44057.0196 | 96.2705 | 88.1353 | 67647.12 | inf | 67647.12 | 67647.12 | 3.3125e+37 | 33823.56 | 88.9297 | 84.4649 | Diode | 10.0587 | 7.7223
Text_H100_Lamma_8B | 3600 | 96181.2709 | inf | 96181.2709 | 96181.2709 | 1.3646e+28 | 48090.6355 | 94.7301 | 87.365 | 70145.6149 | inf | 70145.6149 | 70145.6149 | 2.4998e+38 | 35072.8075 | 88.3306 | 84.1653 | Diode | 10.9796 | 8.0075
Text_H100_SeqLength_1024 | 3600 | 95988.0613 | inf | 95988.0613 | 95988.0613 | 1.3696e+28 | 47994.0307 | 94.7652 | 87.3826 | 69961.8755 | inf | 69961.8755 | 69961.8755 | 2.5071e+38 | 34980.9377 | 88.3738 | 84.1869 | Diode | 10.9575 | 7.9865
Text_H100_SeqLength_2048 | 3600 | 96181.2709 | inf | 96181.2709 | 96181.2709 | 1.3646e+28 | 48090.6355 | 94.7301 | 87.365 | 70145.6149 | inf | 70145.6149 | 70145.6149 | 2.4998e+38 | 35072.8075 | 88.3306 | 84.1653 | Diode | 10.9796 | 8.0075
Text_H100_SeqLength_4096 | 3600 | 95988.6881 | inf | 95988.6881 | 95988.6881 | 1.3138e+28 | 47994.344 | 94.765 | 87.3825 | 70035.1375 | inf | 70035.1375 | 70035.1375 | 2.417e+38 | 35017.5687 | 88.3566 | 84.1783 | Diode | 10.9576 | 7.9949