## All_results
scenario | chip | duration_s | P_mean_MW | P_max_MW | P_min_MW | Energy_MWh | Peak_to_mean | Swing_p95_p05_MW | Time_at_high_load_pct | Dominant_period_s | Transitions_per_h | Ramp_p99_MW_per_s | I_IGBT_rms_A | I_IGBT_peak_A | I_Diode_rms_A | I_Diode_peak_A | P_loss_IGBT_mean_W | P_loss_IGBT_max_W | P_loss_IGBT_swing_W | P_loss_Diode_mean_W | P_loss_Diode_max_W | P_loss_Diode_swing_W | Switching_share_pct | Diode_share_pct | Loss_ratio_pct | Tj_IGBT_mean_C | Tj_IGBT_max_C | Tj_IGBT_min_C | Tj_IGBT_swing_K | Tj_Diode_mean_C | Tj_Diode_max_C | Tj_Diode_min_C | Tj_Diode_swing_K | T_case_mean_C | T_case_swing_K | IGBT_cycles_per_h | IGBT_dT_max_K | IGBT_dT_mean_K | IGBT_dT_p95_K | IGBT_cycles_dT_lt5_per_h | IGBT_cycles_dT_5_10_per_h | IGBT_cycles_dT_10_20_per_h | IGBT_cycles_dT_ge20_per_h | IGBT_cycle_Tmean_C | IGBT_cycle_duration_mean_s | IGBT_cycle_duration_p95_s | IGBT_grid_cycles_per_h | IGBT_grid_cycle_dT_mean_K | IGBT_grid_cycle_dT_max_K | IGBT_load_cycles_per_h | IGBT_load_cycle_dT_mean_K | IGBT_load_cycle_dT_max_K | IGBT_load_cycle_Tmean_C | IGBT_load_cycle_duration_mean_s | Diode_cycles_per_h | Diode_dT_max_K | Diode_dT_mean_K | Diode_dT_p95_K | Diode_cycles_dT_lt5_per_h | Diode_cycles_dT_5_10_per_h | Diode_cycles_dT_10_20_per_h | Diode_cycles_dT_ge20_per_h | Diode_cycle_Tmean_C | Diode_cycle_duration_mean_s | Diode_cycle_duration_p95_s | Diode_grid_cycles_per_h | Diode_grid_cycle_dT_mean_K | Diode_grid_cycle_dT_max_K | Diode_load_cycles_per_h | Diode_load_cycle_dT_mean_K | Diode_load_cycle_dT_max_K | Diode_load_cycle_Tmean_C | Diode_load_cycle_duration_mean_s | IGBT_Nf_eq | IGBT_Nf_eq_dT_ge10 | IGBT_Nf_eq_dT_lt10 | IGBT_Nf_eq_load_cycles | IGBT_Nf_eq_grid_cycles | IGBT_Nf_worst_cycle | IGBT_worst_cycle_dT_K | IGBT_worst_cycle_Tmean_C | Diode_Nf_eq | Diode_Nf_eq_dT_ge10 | Diode_Nf_eq_dT_lt10 | Diode_Nf_eq_load_cycles | Diode_Nf_eq_grid_cycles | Diode_Nf_worst_cycle | Diode_worst_cycle_dT_K | Diode_worst_cycle_Tmean_C | Limiting_device
Image_H100_BatchSize_128 | H_100 | 3600 | 0.44828 | 0.86506 | 0.25337 | 0.44828 | 1.9298 | 0.58625 | 33.7089 | 16.0714 | 464 | 1.1514 | 237.0244 | 844.7903 | 70.2707 | 196.1497 | 186.7893 | 369.0614 | 255.0061 | 15.7291 | 30.835 | 21.1708 | 50.7192 | 7.7668 | 0.045177 | 44.982 | 51.6142 | 25 | 17.3244 | 42.2997 | 46.1209 | 25 | 14.9379 | 41.6957 | 14.492 | 180000 | 26.6142 | 0.39908 | 0.76508 | 179980 | 19.5 | 0 | 0.5 | 44.9919 | 0.036122 | 0.013 | 179072.5 | 0.39247 | 0.7887 | 927.5 | 1.6748 | 26.6142 | 45.8172 | 5.1848 | 180000 | 21.1209 | 0.08732 | 0.16579 | 179999.5 | 0 | 0 | 0.5 | 42.3003 | 0.034963 | 0.012 | 179244.5 | 0.086191 | 0.17093 | 755.5 | 0.35522 | 21.1209 | 42.5388 | 5.9892 | 570865375.1383 | 570865377.807 | 1.2212e+17 | 570865375.1383 | 1.319e+30 | 285432688.9035 | 26.6142 | 38.3071 | 3376395114.1011 | 3376395114.1011 | 2.4468e+29 | 3376395114.1011 | 2.1791e+40 | 1688197557.0506 | 21.1209 | 35.5604 | IGBT
Image_H100_BatchSize_256 | H_100 | 3600 | 0.43236 | 0.65396 | 0.25349 | 0.43236 | 1.5125 | 0.39229 | 45.1533 | 18 | 399 | 0.74254 | 216.1582 | 638.6349 | 64.0845 | 148.283 | 178.8793 | 273.9837 | 167.9054 | 15.0991 | 23.0295 | 14.0135 | 51.0723 | 7.7839 | 0.044865 | 44.142 | 49.1012 | 25 | 15.4529 | 41.5746 | 44.9851 | 25 | 14.2033 | 40.9947 | 13.8152 | 180000 | 24.1012 | 0.38191 | 0.57939 | 179999.5 | 0 | 0 | 0.5 | 44.1513 | 0.032856 | 0.013 | 177187 | 0.37629 | 0.5906 | 2813 | 0.73594 | 24.1012 | 45.482 | 1.4689 | 180000 | 19.9851 | 0.083805 | 0.12635 | 179999.5 | 0 | 0.5 | 0 | 41.5751 | 0.032353 | 0.012 | 178596.5 | 0.083062 | 0.12831 | 1403.5 | 0.17831 | 19.9851 | 42.8678 | 2.8198 | 1561833111.7123 | 1561833111.7279 | 1.5635e+20 | 1561833111.7123 | 7.6219e+31 | 780916555.864 | 24.1012 | 37.0506 | 6505456101.3967 | 6505456101.3967 | 9.4955e+31 | 6505456101.3967 | 8.0881e+41 | 3252728050.6984 | 19.9851 | 34.9925 | IGBT
Image_H100_BatchSize_512 | H_100 | 3600 | 0.45261 | 1.1269 | 0.25307 | 0.45261 | 2.4897 | 0.85156 | 16.4356 | 14.0625 | 312 | 1.5462 | 246.2676 | 1100.4691 | 73.011 | 255.5151 | 189.2689 | 491.4769 | 378.7234 | 15.9189 | 40.7672 | 31.217 | 50.5436 | 7.7582 | 0.045334 | 45.2066 | 54.2981 | 25 | 19.3746 | 42.4878 | 46.9963 | 25 | 15.5332 | 41.8767 | 15.0689 | 180000 | 29.2981 | 0.40453 | 1.0305 | 179844 | 155.5 | 0 | 0.5 | 45.2166 | 0.037195 | 0.013 | 177894 | 0.39348 | 1.0582 | 2106 | 1.3382 | 29.2981 | 47.0975 | 2.4035 | 180001 | 21.9963 | 0.088384 | 0.22176 | 180000.5 | 0 | 0 | 0.5 | 42.4884 | 0.037413 | 0.012 | 177865 | 0.086485 | 0.22836 | 2136 | 0.24654 | 21.9963 | 42.919 | 2.3337 | 232260918.3973 | 232261189.957 | 1.9865e+14 | 232260918.3973 | 2.0231e+28 | 116130594.9785 | 29.2981 | 39.6491 | 2119097597.4414 | 2119097597.4414 | 4.1938e+26 | 2119097597.4414 | 5.1493e+38 | 1059548798.7207 | 21.9963 | 35.9982 | IGBT
Image_H100_ImageSize_16 | H_100 | 3600 | 0.36404 | 0.59557 | 0.25435 | 0.36404 | 1.636 | 0.32806 | 32.7044 | 12 | 599 | 0.62063 | 179.4119 | 581.6134 | 53.1903 | 135.0433 | 149.3872 | 248.2574 | 139.7113 | 12.6446 | 20.9026 | 11.6797 | 51.4803 | 7.8038 | 0.044509 | 40.9893 | 45.4721 | 25 | 13.1307 | 38.8465 | 41.7667 | 25 | 11.8765 | 38.3609 | 11.6389 | 180000 | 20.4721 | 0.31868 | 0.52046 | 179999.5 | 0 | 0 | 0.5 | 40.9969 | 0.034335 | 0.013 | 178370.5 | 0.31448 | 0.53055 | 1629.5 | 0.77888 | 20.4721 | 41.4129 | 2.7408 | 180000 | 16.7667 | 0.070163 | 0.11386 | 179999.5 | 0 | 0.5 | 0 | 38.847 | 0.032727 | 0.012 | 179012.5 | 0.069369 | 0.11572 | 987.5 | 0.2141 | 16.7667 | 39.3726 | 4.1433 | 9747139663.6897 | 9747139663.7169 | 3.4947e+21 | 9747139663.6897 | 7.9343e+32 | 4873569831.8585 | 20.4721 | 35.2361 | 61276298010.36 | 61276298010.36 | 3.1124e+33 | 61276298010.36 | 7.6318e+42 | 30638149005.18 | 16.7667 | 33.3834 | IGBT
Image_H100_ImageSize_32 | H_100 | 3600 | 0.44828 | 0.86506 | 0.25337 | 0.44828 | 1.9298 | 0.58625 | 33.7089 | 16.0714 | 464 | 1.1514 | 237.0244 | 844.7903 | 70.2707 | 196.1497 | 186.7893 | 369.0614 | 255.0061 | 15.7291 | 30.835 | 21.1708 | 50.7192 | 7.7668 | 0.045177 | 44.982 | 51.6142 | 25 | 17.3244 | 42.2997 | 46.1209 | 25 | 14.9379 | 41.6957 | 14.492 | 180000 | 26.6142 | 0.39908 | 0.76508 | 179980 | 19.5 | 0 | 0.5 | 44.9919 | 0.036122 | 0.013 | 179072.5 | 0.39247 | 0.7887 | 927.5 | 1.6748 | 26.6142 | 45.8172 | 5.1848 | 180000 | 21.1209 | 0.08732 | 0.16579 | 179999.5 | 0 | 0 | 0.5 | 42.3003 | 0.034963 | 0.012 | 179244.5 | 0.086191 | 0.17093 | 755.5 | 0.35522 | 21.1209 | 42.5388 | 5.9892 | 570865375.1383 | 570865377.807 | 1.2212e+17 | 570865375.1383 | 1.319e+30 | 285432688.9035 | 26.6142 | 38.3071 | 3376395114.1011 | 3376395114.1011 | 2.4468e+29 | 3376395114.1011 | 2.1791e+40 | 1688197557.0506 | 21.1209 | 35.5604 | IGBT
Image_H100_ImageSize_64 | H_100 | 3600 | 0.8439 | 1.1874 | 0.25572 | 0.8439 | 1.407 | 0.9144 | 64.3933 | 21.9512 | 351 | 1.6475 | 431.4624 | 1159.554 | 127.9158 | 269.2338 | 365.4195 | 520.4743 | 408.9504 | 30.3822 | 43.1021 | 33.6482 | 48.8546 | 7.6761 | 0.046901 | 64.0995 | 73.492 | 25 | 31.1259 | 58.8364 | 65.7104 | 25 | 28.6811 | 57.6699 | 28.4584 | 179997 | 48.492 | 0.78368 | 1.1039 | 179821.5 | 175 | 0 | 0.5 | 64.1202 | 0.034719 | 0.013 | 172886.5 | 0.76433 | 1.1446 | 7110.5 | 1.2543 | 48.492 | 66.2294 | 0.64193 | 179997 | 40.7104 | 0.16887 | 0.23626 | 179996.5 | 0 | 0 | 0.5 | 58.8376 | 0.031983 | 0.012 | 174268.5 | 0.16567 | 0.24063 | 5728.5 | 0.2661 | 40.7104 | 62.4487 | 0.68332 | 5782616.8648 | 5782618.0449 | 2.8336e+13 | 5782616.8648 | 9.2426e+26 | 2891309.0224 | 48.492 | 49.246 | 8847838.8297 | 8847838.8297 | 4.5981e+25 | 8847838.8297 | 2.5788e+37 | 4423919.4148 | 40.7104 | 45.3552 | IGBT
Image_H100_ModelSize_128 | H_100 | 3600 | 0.44828 | 0.86506 | 0.25337 | 0.44828 | 1.9298 | 0.58625 | 33.7089 | 16.0714 | 464 | 1.1514 | 237.0244 | 844.7903 | 70.2707 | 196.1497 | 186.7893 | 369.0614 | 255.0061 | 15.7291 | 30.835 | 21.1708 | 50.7192 | 7.7668 | 0.045177 | 44.982 | 51.6142 | 25 | 17.3244 | 42.2997 | 46.1209 | 25 | 14.9379 | 41.6957 | 14.492 | 180000 | 26.6142 | 0.39908 | 0.76508 | 179980 | 19.5 | 0 | 0.5 | 44.9919 | 0.036122 | 0.013 | 179072.5 | 0.39247 | 0.7887 | 927.5 | 1.6748 | 26.6142 | 45.8172 | 5.1848 | 180000 | 21.1209 | 0.08732 | 0.16579 | 179999.5 | 0 | 0 | 0.5 | 42.3003 | 0.034963 | 0.012 | 179244.5 | 0.086191 | 0.17093 | 755.5 | 0.35522 | 21.1209 | 42.5388 | 5.9892 | 570865375.1383 | 570865377.807 | 1.2212e+17 | 570865375.1383 | 1.319e+30 | 285432688.9035 | 26.6142 | 38.3071 | 3376395114.1011 | 3376395114.1011 | 2.4468e+29 | 3376395114.1011 | 2.1791e+40 | 1688197557.0506 | 21.1209 | 35.5604 | IGBT
Image_H100_ModelSize_256 | H_100 | 3600 | 0.5448 | 1.1469 | 0.25563 | 0.5448 | 2.1051 | 0.87487 | 32.9644 | 28.125 | 255 | 1.5647 | 308.7807 | 1120.0008 | 91.5443 | 260.0501 | 231.6484 | 501.0331 | 389.8975 | 19.3756 | 41.5374 | 32.1167 | 49.7294 | 7.7186 | 0.046076 | 49.7624 | 58.9339 | 25 | 22.6099 | 46.4309 | 51.4222 | 25 | 18.5264 | 45.6869 | 18.2842 | 179997 | 33.9339 | 0.49593 | 1.0582 | 179869.5 | 127 | 0 | 0.5 | 49.775 | 0.03401 | 0.013 | 178498.5 | 0.4869 | 1.0955 | 1498.5 | 1.5711 | 33.9339 | 53.522 | 2.9202 | 180000 | 26.4222 | 0.10763 | 0.22694 | 179999.5 | 0 | 0 | 0.5 | 46.4316 | 0.033334 | 0.012 | 179614.5 | 0.10656 | 0.23151 | 385.5 | 0.60907 | 26.4222 | 46.5714 | 10.8728 | 67262877.4085 | 67262946.019 | 6.5942e+13 | 67262877.4085 | 3.8804e+27 | 33631473.0095 | 33.9339 | 41.967 | 306360724.4527 | 306360724.4527 | 4.0673e+25 | 306360724.4527 | 1.1417e+38 | 153180362.2264 | 26.4222 | 38.2111 | IGBT
Image_H100_ModelSize_512 | H_100 | 3600 | 0.55789 | 1.349 | 0.25497 | 0.55789 | 2.418 | 1.0543 | 28.5533 | 81.8182 | 88 | 1.0896 | 333.8535 | 1317.3611 | 98.9776 | 305.8747 | 239.5844 | 599.226 | 476.6221 | 19.9739 | 49.4113 | 39.082 | 49.2501 | 7.6953 | 0.046525 | 50.6219 | 61.9045 | 25 | 24.9589 | 47.1738 | 53.0469 | 25 | 19.1811 | 46.4069 | 18.2834 | 180000 | 36.9045 | 0.51339 | 1.2422 | 179955.5 | 14.5 | 29.5 | 0.5 | 50.6353 | 0.035225 | 0.013 | 177922.5 | 0.50237 | 1.2556 | 2077.5 | 1.4573 | 36.9045 | 55.6942 | 2.3408 | 180000 | 28.0469 | 0.11099 | 0.26505 | 179999.5 | 0 | 0 | 0.5 | 47.1746 | 0.033735 | 0.012 | 179492.5 | 0.10998 | 0.27323 | 507.5 | 0.46839 | 28.0469 | 49.7492 | 8.479 | 35444410.7341 | 35444506.9231 | 1.3061e+13 | 35444410.7341 | 3.2657e+26 | 17722681.7238 | 36.9045 | 43.4523 | 173163778.7422 | 173163778.7422 | 3.7051e+21 | 173163778.7422 | 1.0328e+37 | 86581889.3711 | 28.0469 | 39.0234 | IGBT
Text_H100_BatchSize2 | H_100 | 3600 | 0.55738 | 0.65601 | 0.25271 | 0.55738 | 1.177 | 0.36095 | 88.9067 | 45 | 176 | 0.46491 | 260.401 | 640.6399 | 77.2012 | 148.7485 | 231.9003 | 274.8928 | 154.2087 | 19.5377 | 23.1046 | 12.8781 | 50.7938 | 7.7704 | 0.045111 | 49.8527 | 55.0906 | 25 | 18.3533 | 46.5228 | 51.0233 | 25 | 18.118 | 45.7723 | 18.0853 | 180000 | 30.0906 | 0.49539 | 0.55374 | 179999.5 | 0 | 0 | 0.5 | 49.8649 | 0.040238 | 0.013 | 176935 | 0.49197 | 0.59395 | 3065 | 0.69287 | 30.0906 | 50.0097 | 1.75 | 180000 | 26.0233 | 0.10846 | 0.12106 | 179999.5 | 0 | 0 | 0.5 | 46.5235 | 0.034423 | 0.012 | 176998 | 0.1078 | 0.12997 | 3002 | 0.14726 | 26.0233 | 46.9779 | 1.4149 | 183283401.1394 | 183283401.1397 | 1.1407e+20 | 183283401.1394 | 1.1568e+32 | 91641700.5699 | 30.0906 | 40.0453 | 355988723.0813 | 355988723.0813 | 1.9266e+27 | 355988723.0813 | 1.124e+42 | 177994361.5407 | 26.0233 | 38.0117 | IGBT
Text_H100_BatchSize16 | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473 | 76.7072 | 87.6299 | 25 | 39.2423 | 69.7341 | 78.364 | 25 | 37.8268 | 68.1964 | 37.3445 | 180000 | 62.6299 | 1.0386 | 1.2649 | 179731.5 | 268 | 0 | 0.5 | 76.7353 | 0.039707 | 0.013 | 177094 | 1.0175 | 1.3293 | 2906 | 2.3253 | 62.6299 | 77.5304 | 1.8423 | 180000 | 53.364 | 0.22272 | 0.27023 | 179999.5 | 0 | 0 | 0.5 | 69.7357 | 0.037676 | 0.012 | 177072 | 0.21889 | 0.28515 | 2928 | 0.45442 | 53.364 | 69.9006 | 1.6865 | 1346278.3169 | 1346279.7245 | 1.2876e+12 | 1346278.3169 | 8.7902e+25 | 673139.8622 | 62.6299 | 56.315 | 1646094.6411 | 1646094.6411 | 1.1343e+25 | 1646094.6411 | 3.2069e+36 | 823047.3205 | 53.364 | 51.682 | IGBT
Text_H100_BatchSize32 | H_100 | 3600 | 1.1534 | 1.4317 | 0.26503 | 1.1534 | 1.2413 | 1.0996 | 87.36 | 14.2857 | 503 | 2.5218 | 549.2604 | 1398.1791 | 162.8394 | 324.6396 | 507.5329 | 640.2919 | 500.3092 | 41.978 | 52.6836 | 40.9403 | 48.0943 | 7.6392 | 0.047643 | 79.2422 | 90.618 | 25 | 41.111 | 71.9238 | 81.0042 | 25 | 39.6778 | 70.3123 | 39.3124 | 180000 | 65.618 | 1.0901 | 1.3083 | 179748.5 | 251 | 0 | 0.5 | 79.2718 | 0.041842 | 0.013 | 177469.5 | 1.0691 | 1.3656 | 2530.5 | 2.5628 | 65.618 | 80.0875 | 2.2432 | 180000 | 56.0042 | 0.23343 | 0.27917 | 179999.5 | 0 | 0 | 0.5 | 71.9255 | 0.037128 | 0.012 | 177498.5 | 0.22963 | 0.29123 | 2501.5 | 0.5032 | 56.0042 | 72.3313 | 1.9317 | 1044555.5959 | 1044557.3201 | 632824508304.4346 | 1044555.5959 | 4.4368e+25 | 522278.66 | 65.618 | 57.809 | 1250558.3221 | 1250558.3221 | 5.7949e+24 | 1250558.3221 | 1.7715e+36 | 625279.161 | 56.0042 | 53.0021 | IGBT
Text_H100_Deepspeedds_z1 | H_100 | 3600 | 1.0289 | 1.4743 | 0.25423 | 1.0289 | 1.433 | 1.1809 | 73.1756 | 13.0435 | 1104 | 2.8028 | 506.9762 | 1439.7841 | 150.3034 | 334.2997 | 450.658 | 661.6265 | 540.0433 | 37.3292 | 54.379 | 44.1207 | 48.3099 | 7.6496 | 0.04743 | 73.2022 | 84.9304 | 25 | 37.7598 | 66.706 | 75.1642 | 25 | 35.3337 | 65.2728 | 34.7956 | 180000 | 59.9304 | 0.96752 | 1.3799 | 179414.5 | 582.5 | 2.5 | 0.5 | 73.2283 | 0.037283 | 0.013 | 178618.5 | 0.93195 | 1.398 | 1381.5 | 5.5673 | 59.9304 | 73.8655 | 3.5946 | 180000 | 50.1642 | 0.20755 | 0.29377 | 179999.5 | 0 | 0 | 0.5 | 66.7075 | 0.036666 | 0.012 | 178618.5 | 0.20116 | 0.29783 | 1381.5 | 1.0346 | 50.1642 | 66.7835 | 3.4955 | 1714615.1015 | 1714626.712 | 253214142115.5431 | 1714615.1015 | 3.0534e+25 | 857313.4761 | 59.9304 | 54.9652 | 2361243.23 | 2361243.23 | 1.4759e+24 | 2361243.23 | 1.4036e+36 | 1180621.615 | 50.1642 | 50.0821 | IGBT
Text_H100_Deepspeedds_z2 | H_100 | 3600 | 1.0739 | 1.3964 | 0.25979 | 1.0739 | 1.3003 | 1.0442 | 84.7 | 13.4328 | 559 | 2.1255 | 514.6392 | 1363.7084 | 152.5752 | 316.6359 | 469.8086 | 622.7155 | 472.7041 | 38.9313 | 51.2845 | 38.7437 | 48.3688 | 7.6525 | 0.047372 | 75.2307 | 86.1897 | 25 | 38.1622 | 68.4588 | 76.9483 | 25 | 36.6978 | 66.9642 | 36.4328 | 180000 | 61.1897 | 1.0085 | 1.2456 | 179720 | 279.5 | 0 | 0.5 | 75.2579 | 0.041834 | 0.013 | 176893 | 0.98608 | 1.3472 | 3107 | 2.2866 | 61.1897 | 76.2168 | 1.8476 | 180000 | 51.9483 | 0.21645 | 0.26635 | 179999.5 | 0 | 0 | 0.5 | 68.4604 | 0.03727 | 0.012 | 176879 | 0.21238 | 0.28271 | 3121 | 0.44749 | 51.9483 | 68.6529 | 1.5601 | 1529210.0278 | 1529211.4818 | 1.6084e+12 | 1529210.0278 | 1.2826e+26 | 764605.7409 | 61.1897 | 55.5949 | 1923200.4607 | 1923200.4607 | 1.286e+25 | 1923200.4607 | 4.5154e+36 | 961600.2303 | 51.9483 | 50.9742 | IGBT
Text_H100_Deepspeedds_z3 | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473 | 76.7072 | 87.6299 | 25 | 39.2423 | 69.7341 | 78.364 | 25 | 37.8268 | 68.1964 | 37.3445 | 180000 | 62.6299 | 1.0386 | 1.2649 | 179731.5 | 268 | 0 | 0.5 | 76.7353 | 0.039707 | 0.013 | 177094 | 1.0175 | 1.3293 | 2906 | 2.3253 | 62.6299 | 77.5304 | 1.8423 | 180000 | 53.364 | 0.22272 | 0.27023 | 179999.5 | 0 | 0 | 0.5 | 69.7357 | 0.037676 | 0.012 | 177072 | 0.21889 | 0.28515 | 2928 | 0.45442 | 53.364 | 69.9006 | 1.6865 | 1346278.3169 | 1346279.7245 | 1.2876e+12 | 1346278.3169 | 8.7902e+25 | 673139.8622 | 62.6299 | 56.315 | 1646094.6411 | 1646094.6411 | 1.1343e+25 | 1646094.6411 | 3.2069e+36 | 823047.3205 | 53.364 | 51.682 | IGBT
Text_H100_Lamma_1B | H_100 | 3600 | 0.69104 | 1.1725 | 0.25212 | 0.69104 | 1.6967 | 0.86267 | 50.7711 | 4.9451 | 1423 | 2.0909 | 352.4445 | 1145.0086 | 104.4893 | 265.8566 | 294.3917 | 513.3111 | 384.1786 | 24.6081 | 42.526 | 31.653 | 49.6369 | 7.7141 | 0.046162 | 56.4937 | 65.5312 | 25 | 25.6554 | 52.259 | 58.0945 | 25 | 23.1757 | 51.3141 | 22.8234 | 180000 | 40.5312 | 0.63035 | 1.0421 | 179288.5 | 711 | 0 | 0.5 | 56.5099 | 0.034457 | 0.013 | 178779.5 | 0.60383 | 1.0969 | 1220.5 | 4.5152 | 40.5312 | 57.8819 | 3.6735 | 180000 | 33.0945 | 0.13671 | 0.22426 | 179999.5 | 0 | 0 | 0.5 | 52.2599 | 0.033183 | 0.012 | 178758.5 | 0.13189 | 0.23418 | 1241.5 | 0.83026 | 33.0945 | 52.7977 | 3.3929 | 18239609.4076 | 18239615.7808 | 5.22e+13 | 18239609.4076 | 5.7652e+27 | 9119807.8904 | 40.5312 | 45.2656 | 41099767.0228 | 41099767.0228 | 1.4166e+26 | 41099767.0228 | 1.5417e+38 | 20549883.5114 | 33.0945 | 41.5472 | IGBT
Text_H100_Lamma_3B | H_100 | 3600 | 0.91685 | 1.3174 | 0.25419 | 0.91685 | 1.4368 | 0.99294 | 72.2444 | 8.2569 | 856 | 2.2317 | 454.7773 | 1286.4983 | 134.828 | 298.7087 | 397.7909 | 583.6751 | 447.2455 | 33.0524 | 48.1691 | 36.7157 | 48.7608 | 7.6716 | 0.046992 | 67.6084 | 78.1174 | 25 | 33.1706 | 61.8782 | 69.4999 | 25 | 31.2109 | 60.6089 | 30.794 | 180000 | 53.1174 | 0.85325 | 1.187 | 179571.5 | 428 | 0 | 0.5 | 67.6311 | 0.036226 | 0.013 | 177418.5 | 0.83103 | 1.2444 | 2581.5 | 2.3803 | 53.1174 | 69.0354 | 1.8306 | 180000 | 44.4999 | 0.18372 | 0.25411 | 179999.5 | 0 | 0 | 0.5 | 61.8796 | 0.034527 | 0.012 | 177414.5 | 0.17966 | 0.26644 | 2585.5 | 0.462 | 44.4999 | 62.45 | 1.6871 | 3381057.0717 | 3381060.2673 | 3.5772e+12 | 3381057.0717 | 3.3856e+26 | 1690530.1337 | 53.1174 | 51.5587 | 4924888.7433 | 4924888.7433 | 6.4356e+23 | 4924888.7433 | 1.124e+37 | 2462444.3717 | 44.4999 | 47.2499 | IGBT
Text_H100_Lamma_8B | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473 | 76.7072 | 87.6299 | 25 | 39.2423 | 69.7341 | 78.364 | 25 | 37.8268 | 68.1964 | 37.3445 | 180000 | 62.6299 | 1.0386 | 1.2649 | 179731.5 | 268 | 0 | 0.5 | 76.7353 | 0.039707 | 0.013 | 177094 | 1.0175 | 1.3293 | 2906 | 2.3253 | 62.6299 | 77.5304 | 1.8423 | 180000 | 53.364 | 0.22272 | 0.27023 | 179999.5 | 0 | 0 | 0.5 | 69.7357 | 0.037676 | 0.012 | 177072 | 0.21889 | 0.28515 | 2928 | 0.45442 | 53.364 | 69.9006 | 1.6865 | 1346278.3169 | 1346279.7245 | 1.2876e+12 | 1346278.3169 | 8.7902e+25 | 673139.8622 | 62.6299 | 56.315 | 1646094.6411 | 1646094.6411 | 1.1343e+25 | 1646094.6411 | 3.2069e+36 | 823047.3205 | 53.364 | 51.682 | IGBT
Text_H100_SeqLength_1024 | H_100 | 3600 | 1.1028 | 1.4045 | 0.25894 | 1.1028 | 1.2736 | 1.0592 | 85.7133 | 6.6667 | 544 | 2.1698 | 527.0567 | 1371.6325 | 156.2567 | 318.4758 | 483.4427 | 626.748 | 480.1819 | 40.0343 | 51.6056 | 39.3389 | 48.2716 | 7.6478 | 0.047468 | 76.683 | 87.6407 | 25 | 39.2837 | 69.7137 | 78.4767 | 25 | 37.9524 | 68.1768 | 37.5875 | 180000 | 62.6407 | 1.038 | 1.2642 | 179727.5 | 272 | 0 | 0.5 | 76.711 | 0.041023 | 0.013 | 177113.5 | 1.0166 | 1.3363 | 2886.5 | 2.3511 | 62.6407 | 77.3852 | 1.9369 | 180000 | 53.4767 | 0.2226 | 0.27008 | 179999.5 | 0 | 0 | 0.5 | 69.7153 | 0.03673 | 0.012 | 177091.5 | 0.21872 | 0.2851 | 2908.5 | 0.45897 | 53.4767 | 70.0353 | 1.6404 | 1344812.9423 | 1344814.3316 | 1.3018e+12 | 1344812.9423 | 8.8971e+25 | 672407.1658 | 62.6407 | 56.3204 | 1626279.0104 | 1626279.0104 | 1.1368e+25 | 1626279.0104 | 3.2467e+36 | 813139.5052 | 53.4767 | 51.7383 | IGBT
Text_H100_SeqLength_2048 | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473 | 76.7072 | 87.6299 | 25 | 39.2423 | 69.7341 | 78.364 | 25 | 37.8268 | 68.1964 | 37.3445 | 180000 | 62.6299 | 1.0386 | 1.2649 | 179731.5 | 268 | 0 | 0.5 | 76.7353 | 0.039707 | 0.013 | 177094 | 1.0175 | 1.3293 | 2906 | 2.3253 | 62.6299 | 77.5304 | 1.8423 | 180000 | 53.364 | 0.22272 | 0.27023 | 179999.5 | 0 | 0 | 0.5 | 69.7357 | 0.037676 | 0.012 | 177072 | 0.21889 | 0.28515 | 2928 | 0.45442 | 53.364 | 69.9006 | 1.6865 | 1346278.3169 | 1346279.7245 | 1.2876e+12 | 1346278.3169 | 8.7902e+25 | 673139.8622 | 62.6299 | 56.315 | 1646094.6411 | 1646094.6411 | 1.1343e+25 | 1646094.6411 | 3.2069e+36 | 823047.3205 | 53.364 | 51.682 | IGBT
Text_H100_SeqLength_4096 | H_100 | 3600 | 1.1002 | 1.4021 | 0.26093 | 1.1002 | 1.2744 | 1.0597 | 85.56 | 13.4328 | 536 | 2.2411 | 526.2989 | 1369.2247 | 156.032 | 317.9167 | 482.2831 | 625.5221 | 480.3823 | 39.939 | 51.508 | 39.3557 | 48.2741 | 7.6479 | 0.047465 | 76.5573 | 87.5261 | 25 | 39.1376 | 69.6049 | 78.2451 | 25 | 37.7379 | 68.0717 | 37.2868 | 180000 | 62.5261 | 1.0355 | 1.2643 | 179731.5 | 268 | 0 | 0.5 | 76.5853 | 0.039373 | 0.013 | 177119 | 1.0141 | 1.3331 | 2881 | 2.3488 | 62.5261 | 77.3395 | 1.838 | 180000 | 53.2451 | 0.22207 | 0.27011 | 179999.5 | 0 | 0 | 0.5 | 69.6065 | 0.036838 | 0.012 | 177087 | 0.21819 | 0.28444 | 2913 | 0.45796 | 53.2451 | 69.9407 | 1.6454 | 1358536.3843 | 1358537.813 | 1.2918e+12 | 1358536.3843 | 8.9341e+25 | 679268.9065 | 62.5261 | 56.2631 | 1667358.6093 | 1667358.6093 | 1.1322e+25 | 1667358.6093 | 3.2632e+36 | 833679.3046 | 53.2451 | 51.6225 | IGBT
Image_B200_BatchSize_128 | B_200 | 3600 | 0.65184 | 1.2119 | 0.40032 | 0.65184 | 1.8592 | 0.79231 | 30.1867 | 11.3924 | 632 | 1.5165 | 335.2774 | 1183.4912 | 99.3998 | 274.7918 | 276.8739 | 532.2978 | 359.2093 | 23.1663 | 44.0523 | 29.4277 | 49.7794 | 7.7211 | 0.04603 | 54.6174 | 64.1637 | 25 | 25.4798 | 50.6353 | 56.2361 | 25 | 22.0995 | 49.7457 | 21.4374 | 180000 | 39.1637 | 0.59267 | 1.1251 | 179684 | 315.5 | 0 | 0.5 | 54.6325 | 0.033576 | 0.013 | 179122.5 | 0.58134 | 1.1416 | 877.5 | 2.907 | 39.1637 | 55.5024 | 4.885 | 180000 | 31.2361 | 0.12869 | 0.24109 | 179999.5 | 0 | 0 | 0.5 | 50.6361 | 0.032488 | 0.012 | 179178.5 | 0.12674 | 0.24423 | 821.5 | 0.55363 | 31.2361 | 51.0305 | 4.8995 | 23127076.4102 | 23127079.6506 | 1.6506e+14 | 23127076.4102 | 1.6863e+27 | 11563539.8253 | 39.1637 | 44.5819 | 66347847.8098 | 66347847.8098 | 1.1502e+27 | 66347847.8098 | 5.5628e+37 | 33173923.9049 | 31.2361 | 40.618 | IGBT
Image_B200_BatchSize_256 | B_200 | 3600 | 0.64912 | 1.3949 | 0.40261 | 0.64912 | 2.149 | 0.96041 | 23.8711 | 11.1111 | 647 | 1.9164 | 342 | 1362.2452 | 101.3928 | 316.2962 | 276.5825 | 621.9714 | 441.2811 | 23.1181 | 51.2252 | 35.9993 | 49.6284 | 7.7137 | 0.04617 | 54.5859 | 65.5994 | 25 | 26.5951 | 50.6074 | 56.4065 | 25 | 22.1883 | 49.7197 | 21.4827 | 180000 | 40.5994 | 0.59223 | 1.3011 | 179676.5 | 323 | 0 | 0.5 | 54.6011 | 0.033189 | 0.013 | 179133.5 | 0.57848 | 1.3203 | 866.5 | 3.4339 | 40.5994 | 54.6858 | 4.8854 | 180003 | 31.4065 | 0.12843 | 0.27747 | 180002.5 | 0 | 0 | 0.5 | 50.6083 | 0.032693 | 0.012 | 178961.5 | 0.12603 | 0.28129 | 1041.5 | 0.54063 | 31.4065 | 51.2921 | 3.8945 | 18030188.2289 | 18030244.316 | 5.7961e+12 | 18030188.2289 | 1.9239e+26 | 9015122.158 | 40.5994 | 45.2997 | 63366413.0517 | 63366413.0517 | 5.3078e+25 | 63366413.0517 | 8.5744e+36 | 31683206.5259 | 31.4065 | 40.7033 | IGBT
Image_B200_BatchSize_512 | B_200 | 3600 | 0.65202 | 1.5094 | 0.40186 | 0.65202 | 2.315 | 1.0803 | 20.5644 | 11.1111 | 656 | 2.2058 | 346.9532 | 1474.0627 | 102.8613 | 342.2588 | 278.3131 | 679.3034 | 501.0699 | 23.2491 | 55.7814 | 40.756 | 49.5424 | 7.7095 | 0.04625 | 54.7657 | 66.8449 | 25 | 27.2683 | 50.7615 | 56.7681 | 25 | 22.3269 | 49.8688 | 21.4717 | 180000 | 41.8449 | 0.59604 | 1.4277 | 179672 | 327.5 | 0 | 0.5 | 54.7811 | 0.035063 | 0.013 | 178836 | 0.57997 | 1.457 | 1164 | 3.0651 | 41.8449 | 54.7688 | 3.9608 | 180000 | 31.7681 | 0.12916 | 0.30354 | 179999.5 | 0 | 0 | 0.5 | 50.7623 | 0.034076 | 0.012 | 178715 | 0.12635 | 0.30899 | 1285 | 0.52068 | 31.7681 | 50.986 | 3.3714 | 14705205.1069 | 14705509.6186 | 710145269513.2117 | 14705205.1069 | 4.9301e+25 | 7352754.8093 | 41.8449 | 45.9224 | 57534892.9703 | 57534892.9703 | 6.7499e+24 | 57534892.9703 | 2.6693e+36 | 28767446.4851 | 31.7681 | 40.8841 | IGBT
Image_B200_ImageSize_32 | B_200 | 3600 | 0.65184 | 1.2119 | 0.40032 | 0.65184 | 1.8592 | 0.79231 | 30.1867 | 11.3924 | 632 | 1.5165 | 335.2774 | 1183.4912 | 99.3998 | 274.7918 | 276.8739 | 532.2978 | 359.2093 | 23.1663 | 44.0523 | 29.4277 | 49.7794 | 7.7211 | 0.04603 | 54.6174 | 64.1637 | 25 | 25.4798 | 50.6353 | 56.2361 | 25 | 22.0995 | 49.7457 | 21.4374 | 180000 | 39.1637 | 0.59267 | 1.1251 | 179684 | 315.5 | 0 | 0.5 | 54.6325 | 0.033576 | 0.013 | 179122.5 | 0.58134 | 1.1416 | 877.5 | 2.907 | 39.1637 | 55.5024 | 4.885 | 180000 | 31.2361 | 0.12869 | 0.24109 | 179999.5 | 0 | 0 | 0.5 | 50.6361 | 0.032488 | 0.012 | 179178.5 | 0.12674 | 0.24423 | 821.5 | 0.55363 | 31.2361 | 51.0305 | 4.8995 | 23127076.4102 | 23127079.6506 | 1.6506e+14 | 23127076.4102 | 1.6863e+27 | 11563539.8253 | 39.1637 | 44.5819 | 66347847.8098 | 66347847.8098 | 1.1502e+27 | 66347847.8098 | 5.5628e+37 | 33173923.9049 | 31.2361 | 40.618 | IGBT
Image_B200_ImageSize_64 | B_200 | 3600 | 1.0173 | 1.5695 | 0.4055 | 1.0173 | 1.5429 | 1.126 | 52.9178 | 18.3673 | 392 | 2.073 | 525.7733 | 1532.7628 | 155.8762 | 355.8882 | 449.4157 | 709.7818 | 524.9165 | 37.1237 | 58.1946 | 42.6288 | 47.9091 | 7.6301 | 0.047827 | 73.0722 | 85.8125 | 25 | 39.2499 | 66.5896 | 75.1413 | 25 | 35.3511 | 65.1643 | 34.95 | 180000 | 60.8125 | 0.96562 | 1.4943 | 179804 | 90 | 105.5 | 0.5 | 73.0986 | 0.03289 | 0.013 | 178393 | 0.95303 | 1.5127 | 1607 | 2.3637 | 60.8125 | 75.959 | 2.4896 | 180000 | 50.1413 | 0.20646 | 0.31653 | 179999.5 | 0 | 0 | 0.5 | 66.5911 | 0.029549 | 0.012 | 179190 | 0.20465 | 0.32027 | 810 | 0.60836 | 50.1413 | 68.0991 | 4.1912 | 1581800.1635 | 1581803.5613 | 736384634815.1031 | 1581800.1635 | 3.8163e+24 | 790905.4053 | 60.8125 | 55.4063 | 2367379.9691 | 2367379.9691 | 8.8301e+23 | 2367379.9691 | 2.2258e+35 | 1183689.9846 | 50.1413 | 50.0706 | IGBT
Image_B200_ImageSize_128 | B_200 | 3600 | 1.3126 | 1.5049 | 0.41562 | 1.3126 | 1.1465 | 1.0564 | 86.0489 | 69.2308 | 112 | 1.4001 | 621.8799 | 1469.6426 | 184.3689 | 341.2325 | 585.0244 | 677.019 | 490.6549 | 48.1884 | 55.6003 | 39.892 | 47.4976 | 7.6101 | 0.048241 | 87.5382 | 99.828 | 25 | 47.0926 | 79.0945 | 89.6768 | 25 | 45.9463 | 77.2446 | 45.7872 | 180000 | 74.828 | 1.258 | 1.4199 | 179947.5 | 52 | 0 | 0.5 | 87.573 | 0.039409 | 0.013 | 174641 | 1.2436 | 1.4376 | 5359 | 1.7283 | 74.828 | 87.9209 | 0.99779 | 180000 | 64.6768 | 0.26807 | 0.30248 | 179999.5 | 0 | 0 | 0.5 | 79.0965 | 0.03664 | 0.012 | 173986 | 0.26527 | 0.3062 | 6014 | 0.3491 | 64.6768 | 79.2188 | 0.79799 | 514330.986 | 514331.1842 | 1.3352e+12 | 514330.986 | 5.6585e+24 | 257165.5921 | 74.828 | 62.414 | 564872.3088 | 564872.3088 | 1.0818e+24 | 564872.3088 | 2.7004e+35 | 282436.1544 | 64.6768 | 57.3384 | IGBT
Image_B200_ModelSize_128 | B_200 | 3600 | 0.65184 | 1.2119 | 0.40032 | 0.65184 | 1.8592 | 0.79231 | 30.1867 | 11.3924 | 632 | 1.5165 | 335.2774 | 1183.4912 | 99.3998 | 274.7918 | 276.8739 | 532.2978 | 359.2093 | 23.1663 | 44.0523 | 29.4277 | 49.7794 | 7.7211 | 0.04603 | 54.6174 | 64.1637 | 25 | 25.4798 | 50.6353 | 56.2361 | 25 | 22.0995 | 49.7457 | 21.4374 | 180000 | 39.1637 | 0.59267 | 1.1251 | 179684 | 315.5 | 0 | 0.5 | 54.6325 | 0.033576 | 0.013 | 179122.5 | 0.58134 | 1.1416 | 877.5 | 2.907 | 39.1637 | 55.5024 | 4.885 | 180000 | 31.2361 | 0.12869 | 0.24109 | 179999.5 | 0 | 0 | 0.5 | 50.6361 | 0.032488 | 0.012 | 179178.5 | 0.12674 | 0.24423 | 821.5 | 0.55363 | 31.2361 | 51.0305 | 4.8995 | 23127076.4102 | 23127079.6506 | 1.6506e+14 | 23127076.4102 | 1.6863e+27 | 11563539.8253 | 39.1637 | 44.5819 | 66347847.8098 | 66347847.8098 | 1.1502e+27 | 66347847.8098 | 5.5628e+37 | 33173923.9049 | 31.2361 | 40.618 | IGBT
Image_B200_ModelSize_256 | B_200 | 3600 | 0.73378 | 1.5493 | 0.40232 | 0.73378 | 2.1114 | 1.1258 | 27.96 | 21.9512 | 327 | 1.9052 | 400.8373 | 1512.9948 | 118.8363 | 351.2983 | 317.5277 | 699.4885 | 524.1709 | 26.4059 | 57.3802 | 42.585 | 48.8854 | 7.6776 | 0.046872 | 58.9381 | 71.6379 | 25 | 30.8045 | 54.3654 | 61.1143 | 25 | 25.6095 | 53.3517 | 24.8381 | 180000 | 46.6379 | 0.68092 | 1.4848 | 179836.5 | 69.5 | 93.5 | 0.5 | 58.9561 | 0.032894 | 0.013 | 178970.5 | 0.67118 | 1.5159 | 1029.5 | 2.3735 | 46.6379 | 60.3345 | 4.0942 | 180003 | 36.1143 | 0.14676 | 0.31451 | 180002.5 | 0 | 0 | 0.5 | 54.3665 | 0.032298 | 0.012 | 179256.5 | 0.14519 | 0.31937 | 746.5 | 0.52308 | 36.1143 | 54.3434 | 5.4068 | 7338177.8803 | 7338218.6834 | 1.3197e+12 | 7338177.8803 | 1.1768e+25 | 3669162.3599 | 46.6379 | 48.3189 | 20818743.4831 | 20818743.4831 | 1.1686e+24 | 20818743.4831 | 7.1384e+35 | 10409371.7416 | 36.1143 | 43.0572 | IGBT
Image_B200_ModelSize_512 | B_200 | 3600 | 0.75986 | 1.8138 | 0.40355 | 0.75986 | 2.387 | 1.3778 | 25.1356 | 56.25 | 135 | 1.7137 | 439.1247 | 1771.2967 | 130.1874 | 411.2728 | 333.349 | 836.3348 | 653.9763 | 27.5984 | 68.1519 | 52.8156 | 48.2371 | 7.6461 | 0.047502 | 60.6008 | 76.3242 | 25 | 34.4439 | 55.795 | 63.7862 | 25 | 27.5802 | 54.7356 | 26.4086 | 180000 | 51.3242 | 0.71577 | 1.7617 | 179932 | 4 | 63.5 | 0.5 | 60.6202 | 0.034378 | 0.013 | 176991 | 0.695 | 1.8298 | 3009 | 1.938 | 51.3242 | 67.532 | 1.5552 | 180000 | 38.7862 | 0.15346 | 0.37052 | 179999.5 | 0 | 0 | 0.5 | 55.7961 | 0.034006 | 0.012 | 178813 | 0.1513 | 0.38339 | 1187 | 0.47836 | 38.7862 | 58.7892 | 3.6693 | 4125891.1693 | 4125891.1803 | 1544733548878902 | 4125891.1693 | 6.7088e+23 | 2063741.2796 | 51.3242 | 50.6621 | 12378602.1159 | 12378602.1159 | 3.6459e+20 | 12378602.1159 | 4.7975e+34 | 6189301.0579 | 38.7862 | 44.3931 | IGBT
Text_B200_BatchSize2 | B_200 | 3600 | 0.78157 | 0.88893 | 0.40656 | 0.78157 | 1.1374 | 0.43512 | 88.8667 | 17.3077 | 208 | 0.6297 | 363.8699 | 868.0945 | 107.8766 | 201.5606 | 331.5703 | 380.0128 | 191.981 | 27.7541 | 31.7287 | 15.865 | 49.8391 | 7.724 | 0.045975 | 60.461 | 67.5105 | 25 | 26.1716 | 55.6929 | 61.9268 | 25 | 25.9545 | 54.6272 | 25.7407 | 180000 | 42.5105 | 0.70967 | 0.77549 | 179998 | 1.5 | 0 | 0.5 | 60.4791 | 0.039261 | 0.013 | 177422.5 | 0.70587 | 0.8093 | 2577.5 | 0.97138 | 42.5105 | 60.799 | 1.9892 | 180000 | 36.9268 | 0.15416 | 0.16815 | 179999.5 | 0 | 0 | 0.5 | 55.6939 | 0.033046 | 0.012 | 177636.5 | 0.15344 | 0.17534 | 2363.5 | 0.20862 | 36.9268 | 57.1797 | 1.6607 | 13249410.8128 | 13249410.8129 | 2.2516e+18 | 13249410.8128 | 2.8502e+29 | 6624705.4064 | 42.5105 | 46.2552 | 17647486.2554 | 17647486.2554 | 1.4419e+26 | 17647486.2554 | 4.4228e+39 | 8823743.1277 | 36.9268 | 43.4634 | IGBT
Text_B200_BatchSize16 | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906 | 92.7371 | 109.5892 | 25 | 51.9234 | 83.6374 | 96.6034 | 25 | 49.8905 | 81.6533 | 49.568 | 180000 | 84.5892 | 1.3559 | 1.7888 | 179600 | 4 | 395.5 | 0.5 | 92.7755 | 0.036427 | 0.013 | 177207 | 1.3253 | 1.8783 | 2793 | 3.2966 | 84.5892 | 94.4033 | 1.702 | 180000 | 71.6034 | 0.28739 | 0.37659 | 179996 | 3.5 | 0 | 0.5 | 83.6396 | 0.034384 | 0.012 | 177234 | 0.28186 | 0.39376 | 2766 | 0.64209 | 71.6034 | 84.23 | 1.5661 | 264946.339 | 264946.3391 | 3514479585408696 | 264946.339 | 1.5473e+23 | 132496.2595 | 84.5892 | 67.2946 | 325975.1852 | 325975.1853 | 2387330686108966 | 325975.1852 | 1.2479e+34 | 162987.5926 | 71.6034 | 60.8017 | IGBT
Text_B200_BatchSize32 | B_200 | 3600 | 1.5345 | 1.9612 | 0.41814 | 1.5345 | 1.2781 | 1.4353 | 81.3444 | 9.0909 | 808 | 3.492 | 735.9011 | 1915.2764 | 218.1728 | 444.7031 | 699.2431 | 914.8205 | 688.9342 | 57.192 | 74.2796 | 55.4482 | 46.4812 | 7.5607 | 0.049296 | 99.6934 | 115.8579 | 25 | 56.9342 | 89.5851 | 102.1818 | 25 | 54.6192 | 87.3901 | 54.0141 | 180000 | 90.8579 | 1.5067 | 1.8775 | 179576.5 | 23.5 | 399.5 | 0.5 | 99.7366 | 0.040316 | 0.013 | 177509.5 | 1.4702 | 1.9571 | 2490.5 | 4.1035 | 90.8579 | 100.9629 | 2.1883 | 180000 | 77.1818 | 0.31837 | 0.39458 | 179999.5 | 0 | 0 | 0.5 | 89.5876 | 0.037242 | 0.012 | 177446.5 | 0.3119 | 0.41124 | 2553.5 | 0.76829 | 77.1818 | 90.5515 | 1.9035 | 179267.5469 | 179267.5476 | 4.6476e+13 | 179267.5469 | 5.4955e+22 | 89642.4689 | 90.8579 | 70.4289 | 217586.1085 | 217586.1085 | 1.3256e+22 | 217586.1085 | 4.9293e+33 | 108793.0542 | 77.1818 | 63.5909 | IGBT
Text_B200_Deepspeedds_z1 | B_200 | 3600 | 1.3283 | 2 | 0.40753 | 1.3283 | 1.5057 | 1.4992 | 70.1844 | 7.9646 | 824 | 3.7532 | 658.807 | 1953.1287 | 195.3167 | 453.4919 | 599.3242 | 935.7165 | 719.5298 | 49.1733 | 75.9053 | 57.9123 | 46.9319 | 7.5826 | 0.048823 | 89.6117 | 107.9142 | 25 | 49.8144 | 80.9528 | 94.336 | 25 | 47.584 | 79.0629 | 47.2348 | 180000 | 82.9142 | 1.2902 | 1.8752 | 179583.5 | 5 | 409.5 | 2 | 89.6481 | 0.035808 | 0.013 | 177909.5 | 1.248 | 1.9656 | 2090.5 | 4.8802 | 82.9142 | 91.0528 | 2.2796 | 180000 | 69.336 | 0.27365 | 0.39568 | 179996 | 3.5 | 0 | 0.5 | 80.9549 | 0.034169 | 0.012 | 177918.5 | 0.26609 | 0.41347 | 2081.5 | 0.91997 | 69.336 | 80.8026 | 2.1211 | 295141.0581 | 295141.0581 | 3106485508408247 | 295141.0581 | 1.2831e+23 | 147705.3449 | 82.9142 | 66.4571 | 387709.053 | 387709.0575 | 3.3576e+13 | 387709.053 | 1.1219e+34 | 193854.5287 | 69.336 | 59.668 | IGBT
Text_B200_Deepspeedds_z2 | B_200 | 3600 | 1.3723 | 1.887 | 0.41212 | 1.3723 | 1.3751 | 1.3605 | 74.5778 | 8.5714 | 815 | 3.0408 | 670.5766 | 1842.7441 | 198.8061 | 427.862 | 619.3966 | 875.0846 | 647.762 | 50.8145 | 71.1816 | 52.2643 | 46.9159 | 7.5819 | 0.048839 | 91.5437 | 108.0457 | 25 | 51.1416 | 82.5945 | 95.0856 | 25 | 48.9231 | 80.6424 | 48.5051 | 180000 | 83.0457 | 1.3335 | 1.776 | 179592 | 12 | 395.5 | 0.5 | 91.5814 | 0.037927 | 0.013 | 177247 | 1.3026 | 1.8785 | 2753 | 3.3208 | 83.0457 | 93.031 | 1.8174 | 180000 | 70.0856 | 0.28279 | 0.3741 | 179997 | 2.5 | 0 | 0.5 | 82.5967 | 0.0348 | 0.012 | 177324 | 0.27723 | 0.39476 | 2676 | 0.65124 | 70.0856 | 82.9644 | 1.6377 | 292857.2758 | 292857.2786 | 3.0561e+13 | 292857.2758 | 1.8217e+23 | 146444.2157 | 83.0457 | 66.5229 | 365858.4491 | 365858.4491 | 29256981870388480 | 365858.4491 | 1.4455e+34 | 182929.2245 | 70.0856 | 60.0428 | IGBT
Text_B200_Deepspeedds_z3 | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906 | 92.7371 | 109.5892 | 25 | 51.9234 | 83.6374 | 96.6034 | 25 | 49.8905 | 81.6533 | 49.568 | 180000 | 84.5892 | 1.3559 | 1.7888 | 179600 | 4 | 395.5 | 0.5 | 92.7755 | 0.036427 | 0.013 | 177207 | 1.3253 | 1.8783 | 2793 | 3.2966 | 84.5892 | 94.4033 | 1.702 | 180000 | 71.6034 | 0.28739 | 0.37659 | 179996 | 3.5 | 0 | 0.5 | 83.6396 | 0.034384 | 0.012 | 177234 | 0.28186 | 0.39376 | 2766 | 0.64209 | 71.6034 | 84.23 | 1.5661 | 264946.339 | 264946.3391 | 3514479585408696 | 264946.339 | 1.5473e+23 | 132496.2595 | 84.5892 | 67.2946 | 325975.1852 | 325975.1853 | 2387330686108966 | 325975.1852 | 1.2479e+34 | 162987.5926 | 71.6034 | 60.8017 | IGBT
Text_B200_Lamma_1B | B_200 | 3600 | 0.82231 | 1.3127 | 0.40789 | 0.82231 | 1.5964 | 0.85262 | 48.12 | 4.4776 | 1599 | 2.3255 | 407.3297 | 1281.9597 | 120.7612 | 297.6549 | 353.4174 | 581.3943 | 389.0648 | 29.4564 | 47.9867 | 31.8083 | 49.2121 | 7.6935 | 0.046561 | 62.794 | 73.0262 | 25 | 30.4597 | 57.7067 | 64.4577 | 25 | 27.8954 | 56.5757 | 27.393 | 180000 | 48.0262 | 0.75738 | 1.1927 | 179208 | 791.5 | 0 | 0.5 | 62.8138 | 0.03478 | 0.013 | 178971.5 | 0.72836 | 1.2377 | 1028.5 | 5.8069 | 48.0262 | 63.6511 | 4.4245 | 180000 | 39.4577 | 0.16368 | 0.25552 | 179999.5 | 0 | 0 | 0.5 | 57.7078 | 0.032385 | 0.012 | 178995.5 | 0.15849 | 0.26523 | 1004.5 | 1.0897 | 39.4577 | 58.2073 | 4.0553 | 6132192.7229 | 6132194.2522 | 2.4589e+13 | 6132192.7229 | 5.5541e+26 | 3066097.1261 | 48.0262 | 49.0131 | 10975371.1343 | 10975371.1343 | 1.3687e+26 | 10975371.1343 | 1.9129e+37 | 5487685.5672 | 39.4577 | 44.7289 | IGBT
Text_B200_Lamma_3B | B_200 | 3600 | 1.0446 | 1.6056 | 0.40919 | 1.0446 | 1.5371 | 1.1156 | 56.9089 | 6.8702 | 1039 | 2.5454 | 523.0716 | 1568.0157 | 155.0752 | 364.0735 | 459.733 | 728.2121 | 520.2929 | 38.0228 | 59.6509 | 42.2472 | 48.0879 | 7.6388 | 0.047649 | 74.2053 | 87.3781 | 25 | 38.8831 | 67.576 | 76.6185 | 25 | 36.032 | 66.1161 | 35.6066 | 180000 | 62.3781 | 0.98743 | 1.4873 | 179480.5 | 509 | 10 | 0.5 | 74.2322 | 0.035007 | 0.013 | 178237.5 | 0.95861 | 1.5784 | 1762.5 | 3.9024 | 62.3781 | 76.4345 | 2.593 | 180000 | 51.6185 | 0.21144 | 0.31569 | 179999.5 | 0 | 0 | 0.5 | 67.5776 | 0.033181 | 0.012 | 178249.5 | 0.20626 | 0.33443 | 1750.5 | 0.7385 | 51.6185 | 68.1777 | 2.385 | 1376138.1486 | 1376148.0935 | 190424353652.7401 | 1376138.1486 | 7.007e+24 | 688074.9638 | 62.3781 | 56.189 | 1995839.89 | 1995839.89 | 3.3881e+21 | 1995839.89 | 3.7945e+35 | 997919.945 | 51.6185 | 50.8093 | IGBT
Text_B200_Lamma_8B | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906 | 92.7371 | 109.5892 | 25 | 51.9234 | 83.6374 | 96.6034 | 25 | 49.8905 | 81.6533 | 49.568 | 180000 | 84.5892 | 1.3559 | 1.7888 | 179600 | 4 | 395.5 | 0.5 | 92.7755 | 0.036427 | 0.013 | 177207 | 1.3253 | 1.8783 | 2793 | 3.2966 | 84.5892 | 94.4033 | 1.702 | 180000 | 71.6034 | 0.28739 | 0.37659 | 179996 | 3.5 | 0 | 0.5 | 83.6396 | 0.034384 | 0.012 | 177234 | 0.28186 | 0.39376 | 2766 | 0.64209 | 71.6034 | 84.23 | 1.5661 | 264946.339 | 264946.3391 | 3514479585408696 | 264946.339 | 1.5473e+23 | 132496.2595 | 84.5892 | 67.2946 | 325975.1852 | 325975.1853 | 2387330686108966 | 325975.1852 | 1.2479e+34 | 162987.5926 | 71.6034 | 60.8017 | IGBT
Text_B200_SeqLength_1024 | B_200 | 3600 | 1.3928 | 1.8798 | 0.4125 | 1.3928 | 1.3497 | 1.3656 | 75.46 | 8.7379 | 792 | 3.1259 | 678.8393 | 1835.7063 | 201.2557 | 426.2279 | 629.4087 | 871.2503 | 651.0014 | 51.6161 | 70.8822 | 52.5049 | 46.8606 | 7.5792 | 0.048897 | 92.5375 | 108.7878 | 25 | 51.9414 | 83.443 | 95.8617 | 25 | 49.5812 | 81.4605 | 49.214 | 180000 | 83.7878 | 1.3552 | 1.7883 | 179596 | 8 | 395.5 | 0.5 | 92.5758 | 0.03696 | 0.013 | 177194 | 1.3243 | 1.8815 | 2806 | 3.3033 | 83.7878 | 94.2073 | 1.7308 | 180000 | 70.8617 | 0.28726 | 0.37655 | 179997 | 2.5 | 0 | 0.5 | 83.4452 | 0.035015 | 0.012 | 177168 | 0.28167 | 0.39577 | 2832 | 0.63693 | 70.8617 | 84.1816 | 1.5717 | 279036.886 | 279036.886 | 59709794879900968 | 279036.886 | 1.5783e+23 | 139530.8919 | 83.7878 | 66.8939 | 344778.1838 | 344778.1838 | 3.4483e+17 | 344778.1838 | 1.2714e+34 | 172389.0919 | 70.8617 | 60.4309 | IGBT
Text_B200_SeqLength_2048 | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906 | 92.7371 | 109.5892 | 25 | 51.9234 | 83.6374 | 96.6034 | 25 | 49.8905 | 81.6533 | 49.568 | 180000 | 84.5892 | 1.3559 | 1.7888 | 179600 | 4 | 395.5 | 0.5 | 92.7755 | 0.036427 | 0.013 | 177207 | 1.3253 | 1.8783 | 2793 | 3.2966 | 84.5892 | 94.4033 | 1.702 | 180000 | 71.6034 | 0.28739 | 0.37659 | 179996 | 3.5 | 0 | 0.5 | 83.6396 | 0.034384 | 0.012 | 177234 | 0.28186 | 0.39376 | 2766 | 0.64209 | 71.6034 | 84.23 | 1.5661 | 264946.339 | 264946.3391 | 3514479585408696 | 264946.339 | 1.5473e+23 | 132496.2595 | 84.5892 | 67.2946 | 325975.1852 | 325975.1853 | 2387330686108966 | 325975.1852 | 1.2479e+34 | 162987.5926 | 71.6034 | 60.8017 | IGBT
Text_B200_SeqLength_4096 | B_200 | 3600 | 1.394 | 1.8821 | 0.41118 | 1.394 | 1.3502 | 1.3675 | 75.2956 | 8.6538 | 792 | 3.1524 | 679.5989 | 1837.9769 | 201.4809 | 426.7551 | 630.0543 | 872.4869 | 651.9624 | 51.6662 | 70.9788 | 52.5811 | 46.8527 | 7.5788 | 0.048905 | 92.6408 | 109.184 | 25 | 51.9826 | 83.5368 | 96.1343 | 25 | 49.7394 | 81.5522 | 49.2714 | 180000 | 84.184 | 1.3566 | 1.7903 | 179597 | 7 | 395.5 | 0.5 | 92.6792 | 0.037406 | 0.013 | 177220 | 1.3259 | 1.8627 | 2780 | 3.3149 | 84.184 | 94.3808 | 1.7762 | 180000 | 71.1343 | 0.28754 | 0.37691 | 179997 | 2.5 | 0 | 0.5 | 83.539 | 0.03431 | 0.012 | 177200 | 0.28198 | 0.39129 | 2800 | 0.63976 | 71.1343 | 84.1997 | 1.5434 | 271971.3384 | 271971.3384 | 22967122419626672 | 271971.3384 | 1.5486e+23 | 135999.5707 | 84.184 | 67.092 | 337721.6537 | 337721.6537 | 79922704799301968 | 337721.6537 | 1.2506e+34 | 168860.8269 | 71.1343 | 60.5671 | IGBT

## Load_characteristics
scenario | chip | duration_s | P_mean_MW | P_max_MW | P_min_MW | Energy_MWh | Peak_to_mean | Swing_p95_p05_MW | Time_at_high_load_pct | Dominant_period_s | Transitions_per_h | Ramp_p99_MW_per_s
Image_H100_BatchSize_128 | H_100 | 3600 | 0.44828 | 0.86506 | 0.25337 | 0.44828 | 1.9298 | 0.58625 | 33.7089 | 16.0714 | 464 | 1.1514
Image_H100_BatchSize_256 | H_100 | 3600 | 0.43236 | 0.65396 | 0.25349 | 0.43236 | 1.5125 | 0.39229 | 45.1533 | 18 | 399 | 0.74254
Image_H100_BatchSize_512 | H_100 | 3600 | 0.45261 | 1.1269 | 0.25307 | 0.45261 | 2.4897 | 0.85156 | 16.4356 | 14.0625 | 312 | 1.5462
Image_H100_ImageSize_16 | H_100 | 3600 | 0.36404 | 0.59557 | 0.25435 | 0.36404 | 1.636 | 0.32806 | 32.7044 | 12 | 599 | 0.62063
Image_H100_ImageSize_32 | H_100 | 3600 | 0.44828 | 0.86506 | 0.25337 | 0.44828 | 1.9298 | 0.58625 | 33.7089 | 16.0714 | 464 | 1.1514
Image_H100_ImageSize_64 | H_100 | 3600 | 0.8439 | 1.1874 | 0.25572 | 0.8439 | 1.407 | 0.9144 | 64.3933 | 21.9512 | 351 | 1.6475
Image_H100_ModelSize_128 | H_100 | 3600 | 0.44828 | 0.86506 | 0.25337 | 0.44828 | 1.9298 | 0.58625 | 33.7089 | 16.0714 | 464 | 1.1514
Image_H100_ModelSize_256 | H_100 | 3600 | 0.5448 | 1.1469 | 0.25563 | 0.5448 | 2.1051 | 0.87487 | 32.9644 | 28.125 | 255 | 1.5647
Image_H100_ModelSize_512 | H_100 | 3600 | 0.55789 | 1.349 | 0.25497 | 0.55789 | 2.418 | 1.0543 | 28.5533 | 81.8182 | 88 | 1.0896
Text_H100_BatchSize2 | H_100 | 3600 | 0.55738 | 0.65601 | 0.25271 | 0.55738 | 1.177 | 0.36095 | 88.9067 | 45 | 176 | 0.46491
Text_H100_BatchSize16 | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414
Text_H100_BatchSize32 | H_100 | 3600 | 1.1534 | 1.4317 | 0.26503 | 1.1534 | 1.2413 | 1.0996 | 87.36 | 14.2857 | 503 | 2.5218
Text_H100_Deepspeedds_z1 | H_100 | 3600 | 1.0289 | 1.4743 | 0.25423 | 1.0289 | 1.433 | 1.1809 | 73.1756 | 13.0435 | 1104 | 2.8028
Text_H100_Deepspeedds_z2 | H_100 | 3600 | 1.0739 | 1.3964 | 0.25979 | 1.0739 | 1.3003 | 1.0442 | 84.7 | 13.4328 | 559 | 2.1255
Text_H100_Deepspeedds_z3 | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414
Text_H100_Lamma_1B | H_100 | 3600 | 0.69104 | 1.1725 | 0.25212 | 0.69104 | 1.6967 | 0.86267 | 50.7711 | 4.9451 | 1423 | 2.0909
Text_H100_Lamma_3B | H_100 | 3600 | 0.91685 | 1.3174 | 0.25419 | 0.91685 | 1.4368 | 0.99294 | 72.2444 | 8.2569 | 856 | 2.2317
Text_H100_Lamma_8B | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414
Text_H100_SeqLength_1024 | H_100 | 3600 | 1.1028 | 1.4045 | 0.25894 | 1.1028 | 1.2736 | 1.0592 | 85.7133 | 6.6667 | 544 | 2.1698
Text_H100_SeqLength_2048 | H_100 | 3600 | 1.1033 | 1.3982 | 0.26056 | 1.1033 | 1.2673 | 1.0603 | 85.6422 | 13.4328 | 536 | 2.3414
Text_H100_SeqLength_4096 | H_100 | 3600 | 1.1002 | 1.4021 | 0.26093 | 1.1002 | 1.2744 | 1.0597 | 85.56 | 13.4328 | 536 | 2.2411
Image_B200_BatchSize_128 | B_200 | 3600 | 0.65184 | 1.2119 | 0.40032 | 0.65184 | 1.8592 | 0.79231 | 30.1867 | 11.3924 | 632 | 1.5165
Image_B200_BatchSize_256 | B_200 | 3600 | 0.64912 | 1.3949 | 0.40261 | 0.64912 | 2.149 | 0.96041 | 23.8711 | 11.1111 | 647 | 1.9164
Image_B200_BatchSize_512 | B_200 | 3600 | 0.65202 | 1.5094 | 0.40186 | 0.65202 | 2.315 | 1.0803 | 20.5644 | 11.1111 | 656 | 2.2058
Image_B200_ImageSize_32 | B_200 | 3600 | 0.65184 | 1.2119 | 0.40032 | 0.65184 | 1.8592 | 0.79231 | 30.1867 | 11.3924 | 632 | 1.5165
Image_B200_ImageSize_64 | B_200 | 3600 | 1.0173 | 1.5695 | 0.4055 | 1.0173 | 1.5429 | 1.126 | 52.9178 | 18.3673 | 392 | 2.073
Image_B200_ImageSize_128 | B_200 | 3600 | 1.3126 | 1.5049 | 0.41562 | 1.3126 | 1.1465 | 1.0564 | 86.0489 | 69.2308 | 112 | 1.4001
Image_B200_ModelSize_128 | B_200 | 3600 | 0.65184 | 1.2119 | 0.40032 | 0.65184 | 1.8592 | 0.79231 | 30.1867 | 11.3924 | 632 | 1.5165
Image_B200_ModelSize_256 | B_200 | 3600 | 0.73378 | 1.5493 | 0.40232 | 0.73378 | 2.1114 | 1.1258 | 27.96 | 21.9512 | 327 | 1.9052
Image_B200_ModelSize_512 | B_200 | 3600 | 0.75986 | 1.8138 | 0.40355 | 0.75986 | 2.387 | 1.3778 | 25.1356 | 56.25 | 135 | 1.7137
Text_B200_BatchSize2 | B_200 | 3600 | 0.78157 | 0.88893 | 0.40656 | 0.78157 | 1.1374 | 0.43512 | 88.8667 | 17.3077 | 208 | 0.6297
Text_B200_BatchSize16 | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949
Text_B200_BatchSize32 | B_200 | 3600 | 1.5345 | 1.9612 | 0.41814 | 1.5345 | 1.2781 | 1.4353 | 81.3444 | 9.0909 | 808 | 3.492
Text_B200_Deepspeedds_z1 | B_200 | 3600 | 1.3283 | 2 | 0.40753 | 1.3283 | 1.5057 | 1.4992 | 70.1844 | 7.9646 | 824 | 3.7532
Text_B200_Deepspeedds_z2 | B_200 | 3600 | 1.3723 | 1.887 | 0.41212 | 1.3723 | 1.3751 | 1.3605 | 74.5778 | 8.5714 | 815 | 3.0408
Text_B200_Deepspeedds_z3 | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949
Text_B200_Lamma_1B | B_200 | 3600 | 0.82231 | 1.3127 | 0.40789 | 0.82231 | 1.5964 | 0.85262 | 48.12 | 4.4776 | 1599 | 2.3255
Text_B200_Lamma_3B | B_200 | 3600 | 1.0446 | 1.6056 | 0.40919 | 1.0446 | 1.5371 | 1.1156 | 56.9089 | 6.8702 | 1039 | 2.5454
Text_B200_Lamma_8B | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949
Text_B200_SeqLength_1024 | B_200 | 3600 | 1.3928 | 1.8798 | 0.4125 | 1.3928 | 1.3497 | 1.3656 | 75.46 | 8.7379 | 792 | 3.1259
Text_B200_SeqLength_2048 | B_200 | 3600 | 1.3932 | 1.8827 | 0.41056 | 1.3932 | 1.3513 | 1.3765 | 75.4422 | 8.4906 | 800 | 3.0949
Text_B200_SeqLength_4096 | B_200 | 3600 | 1.394 | 1.8821 | 0.41118 | 1.394 | 1.3502 | 1.3675 | 75.2956 | 8.6538 | 792 | 3.1524

## Electrical_characteristics
scenario | I_IGBT_rms_A | I_IGBT_peak_A | I_Diode_rms_A | I_Diode_peak_A | P_loss_IGBT_mean_W | P_loss_IGBT_max_W | P_loss_IGBT_swing_W | P_loss_Diode_mean_W | P_loss_Diode_max_W | P_loss_Diode_swing_W | Switching_share_pct | Diode_share_pct | Loss_ratio_pct
Image_B200_BatchSize_128 | 335.2774 | 1183.4912 | 99.3998 | 274.7918 | 276.8739 | 532.2978 | 359.2093 | 23.1663 | 44.0523 | 29.4277 | 49.7794 | 7.7211 | 0.04603
Image_B200_BatchSize_256 | 342 | 1362.2452 | 101.3928 | 316.2962 | 276.5825 | 621.9714 | 441.2811 | 23.1181 | 51.2252 | 35.9993 | 49.6284 | 7.7137 | 0.04617
Image_B200_BatchSize_512 | 346.9532 | 1474.0627 | 102.8613 | 342.2588 | 278.3131 | 679.3034 | 501.0699 | 23.2491 | 55.7814 | 40.756 | 49.5424 | 7.7095 | 0.04625
Image_B200_ImageSize_128 | 621.8799 | 1469.6426 | 184.3689 | 341.2325 | 585.0244 | 677.019 | 490.6549 | 48.1884 | 55.6003 | 39.892 | 47.4976 | 7.6101 | 0.048241
Image_B200_ImageSize_32 | 335.2774 | 1183.4912 | 99.3998 | 274.7918 | 276.8739 | 532.2978 | 359.2093 | 23.1663 | 44.0523 | 29.4277 | 49.7794 | 7.7211 | 0.04603
Image_B200_ImageSize_64 | 525.7733 | 1532.7628 | 155.8762 | 355.8882 | 449.4157 | 709.7818 | 524.9165 | 37.1237 | 58.1946 | 42.6288 | 47.9091 | 7.6301 | 0.047827
Image_B200_ModelSize_128 | 335.2774 | 1183.4912 | 99.3998 | 274.7918 | 276.8739 | 532.2978 | 359.2093 | 23.1663 | 44.0523 | 29.4277 | 49.7794 | 7.7211 | 0.04603
Image_B200_ModelSize_256 | 400.8373 | 1512.9948 | 118.8363 | 351.2983 | 317.5277 | 699.4885 | 524.1709 | 26.4059 | 57.3802 | 42.585 | 48.8854 | 7.6776 | 0.046872
Image_B200_ModelSize_512 | 439.1247 | 1771.2967 | 130.1874 | 411.2728 | 333.349 | 836.3348 | 653.9763 | 27.5984 | 68.1519 | 52.8156 | 48.2371 | 7.6461 | 0.047502
Image_H100_BatchSize_128 | 237.0244 | 844.7903 | 70.2707 | 196.1497 | 186.7893 | 369.0614 | 255.0061 | 15.7291 | 30.835 | 21.1708 | 50.7192 | 7.7668 | 0.045177
Image_H100_BatchSize_256 | 216.1582 | 638.6349 | 64.0845 | 148.283 | 178.8793 | 273.9837 | 167.9054 | 15.0991 | 23.0295 | 14.0135 | 51.0723 | 7.7839 | 0.044865
Image_H100_BatchSize_512 | 246.2676 | 1100.4691 | 73.011 | 255.5151 | 189.2689 | 491.4769 | 378.7234 | 15.9189 | 40.7672 | 31.217 | 50.5436 | 7.7582 | 0.045334
Image_H100_ImageSize_16 | 179.4119 | 581.6134 | 53.1903 | 135.0433 | 149.3872 | 248.2574 | 139.7113 | 12.6446 | 20.9026 | 11.6797 | 51.4803 | 7.8038 | 0.044509
Image_H100_ImageSize_32 | 237.0244 | 844.7903 | 70.2707 | 196.1497 | 186.7893 | 369.0614 | 255.0061 | 15.7291 | 30.835 | 21.1708 | 50.7192 | 7.7668 | 0.045177
Image_H100_ImageSize_64 | 431.4624 | 1159.554 | 127.9158 | 269.2338 | 365.4195 | 520.4743 | 408.9504 | 30.3822 | 43.1021 | 33.6482 | 48.8546 | 7.6761 | 0.046901
Image_H100_ModelSize_128 | 237.0244 | 844.7903 | 70.2707 | 196.1497 | 186.7893 | 369.0614 | 255.0061 | 15.7291 | 30.835 | 21.1708 | 50.7192 | 7.7668 | 0.045177
Image_H100_ModelSize_256 | 308.7807 | 1120.0008 | 91.5443 | 260.0501 | 231.6484 | 501.0331 | 389.8975 | 19.3756 | 41.5374 | 32.1167 | 49.7294 | 7.7186 | 0.046076
Image_H100_ModelSize_512 | 333.8535 | 1317.3611 | 98.9776 | 305.8747 | 239.5844 | 599.226 | 476.6221 | 19.9739 | 49.4113 | 39.082 | 49.2501 | 7.6953 | 0.046525
Text_B200_BatchSize16 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906
Text_B200_BatchSize2 | 363.8699 | 868.0945 | 107.8766 | 201.5606 | 331.5703 | 380.0128 | 191.981 | 27.7541 | 31.7287 | 15.865 | 49.8391 | 7.724 | 0.045975
Text_B200_BatchSize32 | 735.9011 | 1915.2764 | 218.1728 | 444.7031 | 699.2431 | 914.8205 | 688.9342 | 57.192 | 74.2796 | 55.4482 | 46.4812 | 7.5607 | 0.049296
Text_B200_Deepspeedds_z1 | 658.807 | 1953.1287 | 195.3167 | 453.4919 | 599.3242 | 935.7165 | 719.5298 | 49.1733 | 75.9053 | 57.9123 | 46.9319 | 7.5826 | 0.048823
Text_B200_Deepspeedds_z2 | 670.5766 | 1842.7441 | 198.8061 | 427.862 | 619.3966 | 875.0846 | 647.762 | 50.8145 | 71.1816 | 52.2643 | 46.9159 | 7.5819 | 0.048839
Text_B200_Deepspeedds_z3 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906
Text_B200_Lamma_1B | 407.3297 | 1281.9597 | 120.7612 | 297.6549 | 353.4174 | 581.3943 | 389.0648 | 29.4564 | 47.9867 | 31.8083 | 49.2121 | 7.6935 | 0.046561
Text_B200_Lamma_3B | 523.0716 | 1568.0157 | 155.0752 | 364.0735 | 459.733 | 728.2121 | 520.2929 | 38.0228 | 59.6509 | 42.2472 | 48.0879 | 7.6388 | 0.047649
Text_B200_Lamma_8B | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906
Text_B200_SeqLength_1024 | 678.8393 | 1835.7063 | 201.2557 | 426.2279 | 629.4087 | 871.2503 | 651.0014 | 51.6161 | 70.8822 | 52.5049 | 46.8606 | 7.5792 | 0.048897
Text_B200_SeqLength_2048 | 679.4341 | 1838.5394 | 201.432 | 426.8857 | 629.7318 | 872.7933 | 655.6763 | 51.6397 | 71.0027 | 52.895 | 46.8525 | 7.5788 | 0.048906
Text_B200_SeqLength_4096 | 679.5989 | 1837.9769 | 201.4809 | 426.7551 | 630.0543 | 872.4869 | 651.9624 | 51.6662 | 70.9788 | 52.5811 | 46.8527 | 7.5788 | 0.048905
Text_H100_BatchSize16 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473
Text_H100_BatchSize2 | 260.401 | 640.6399 | 77.2012 | 148.7485 | 231.9003 | 274.8928 | 154.2087 | 19.5377 | 23.1046 | 12.8781 | 50.7938 | 7.7704 | 0.045111
Text_H100_BatchSize32 | 549.2604 | 1398.1791 | 162.8394 | 324.6396 | 507.5329 | 640.2919 | 500.3092 | 41.978 | 52.6836 | 40.9403 | 48.0943 | 7.6392 | 0.047643
Text_H100_Deepspeedds_z1 | 506.9762 | 1439.7841 | 150.3034 | 334.2997 | 450.658 | 661.6265 | 540.0433 | 37.3292 | 54.379 | 44.1207 | 48.3099 | 7.6496 | 0.04743
Text_H100_Deepspeedds_z2 | 514.6392 | 1363.7084 | 152.5752 | 316.6359 | 469.8086 | 622.7155 | 472.7041 | 38.9313 | 51.2845 | 38.7437 | 48.3688 | 7.6525 | 0.047372
Text_H100_Deepspeedds_z3 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473
Text_H100_Lamma_1B | 352.4445 | 1145.0086 | 104.4893 | 265.8566 | 294.3917 | 513.3111 | 384.1786 | 24.6081 | 42.526 | 31.653 | 49.6369 | 7.7141 | 0.046162
Text_H100_Lamma_3B | 454.7773 | 1286.4983 | 134.828 | 298.7087 | 397.7909 | 583.6751 | 447.2455 | 33.0524 | 48.1691 | 36.7157 | 48.7608 | 7.6716 | 0.046992
Text_H100_Lamma_8B | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473
Text_H100_SeqLength_1024 | 527.0567 | 1371.6325 | 156.2567 | 318.4758 | 483.4427 | 626.748 | 480.1819 | 40.0343 | 51.6056 | 39.3389 | 48.2716 | 7.6478 | 0.047468
Text_H100_SeqLength_2048 | 527.496 | 1365.3846 | 156.3869 | 317.0251 | 483.7151 | 623.5681 | 480.689 | 40.0553 | 51.3524 | 39.3798 | 48.266 | 7.6475 | 0.047473
Text_H100_SeqLength_4096 | 526.2989 | 1369.2247 | 156.032 | 317.9167 | 482.2831 | 625.5221 | 480.3823 | 39.939 | 51.508 | 39.3557 | 48.2741 | 7.6479 | 0.047465

## Thermal_characteristics
scenario | Tj_IGBT_mean_C | Tj_IGBT_max_C | Tj_IGBT_min_C | Tj_IGBT_swing_K | Tj_Diode_mean_C | Tj_Diode_max_C | Tj_Diode_min_C | Tj_Diode_swing_K | T_case_mean_C | T_case_swing_K | IGBT_cycles_per_h | IGBT_dT_max_K | IGBT_dT_mean_K | IGBT_dT_p95_K | IGBT_cycles_dT_lt5_per_h | IGBT_cycles_dT_5_10_per_h | IGBT_cycles_dT_10_20_per_h | IGBT_cycles_dT_ge20_per_h | IGBT_cycle_Tmean_C | IGBT_cycle_duration_mean_s | IGBT_cycle_duration_p95_s | IGBT_grid_cycles_per_h | IGBT_grid_cycle_dT_mean_K | IGBT_grid_cycle_dT_max_K | IGBT_load_cycles_per_h | IGBT_load_cycle_dT_mean_K | IGBT_load_cycle_dT_max_K | IGBT_load_cycle_Tmean_C | IGBT_load_cycle_duration_mean_s | Diode_cycles_per_h | Diode_dT_max_K | Diode_dT_mean_K | Diode_dT_p95_K | Diode_cycles_dT_lt5_per_h | Diode_cycles_dT_5_10_per_h | Diode_cycles_dT_10_20_per_h | Diode_cycles_dT_ge20_per_h | Diode_cycle_Tmean_C | Diode_cycle_duration_mean_s | Diode_cycle_duration_p95_s | Diode_grid_cycles_per_h | Diode_grid_cycle_dT_mean_K | Diode_grid_cycle_dT_max_K | Diode_load_cycles_per_h | Diode_load_cycle_dT_mean_K | Diode_load_cycle_dT_max_K | Diode_load_cycle_Tmean_C | Diode_load_cycle_duration_mean_s
Image_B200_BatchSize_128 | 54.6174 | 64.1637 | 25 | 25.4798 | 50.6353 | 56.2361 | 25 | 22.0995 | 49.7457 | 21.4374 | 180000 | 39.1637 | 0.59267 | 1.1251 | 179684 | 315.5 | 0 | 0.5 | 54.6325 | 0.033576 | 0.013 | 179122.5 | 0.58134 | 1.1416 | 877.5 | 2.907 | 39.1637 | 55.5024 | 4.885 | 180000 | 31.2361 | 0.12869 | 0.24109 | 179999.5 | 0 | 0 | 0.5 | 50.6361 | 0.032488 | 0.012 | 179178.5 | 0.12674 | 0.24423 | 821.5 | 0.55363 | 31.2361 | 51.0305 | 4.8995
Image_B200_BatchSize_256 | 54.5859 | 65.5994 | 25 | 26.5951 | 50.6074 | 56.4065 | 25 | 22.1883 | 49.7197 | 21.4827 | 180000 | 40.5994 | 0.59223 | 1.3011 | 179676.5 | 323 | 0 | 0.5 | 54.6011 | 0.033189 | 0.013 | 179133.5 | 0.57848 | 1.3203 | 866.5 | 3.4339 | 40.5994 | 54.6858 | 4.8854 | 180003 | 31.4065 | 0.12843 | 0.27747 | 180002.5 | 0 | 0 | 0.5 | 50.6083 | 0.032693 | 0.012 | 178961.5 | 0.12603 | 0.28129 | 1041.5 | 0.54063 | 31.4065 | 51.2921 | 3.8945
Image_B200_BatchSize_512 | 54.7657 | 66.8449 | 25 | 27.2683 | 50.7615 | 56.7681 | 25 | 22.3269 | 49.8688 | 21.4717 | 180000 | 41.8449 | 0.59604 | 1.4277 | 179672 | 327.5 | 0 | 0.5 | 54.7811 | 0.035063 | 0.013 | 178836 | 0.57997 | 1.457 | 1164 | 3.0651 | 41.8449 | 54.7688 | 3.9608 | 180000 | 31.7681 | 0.12916 | 0.30354 | 179999.5 | 0 | 0 | 0.5 | 50.7623 | 0.034076 | 0.012 | 178715 | 0.12635 | 0.30899 | 1285 | 0.52068 | 31.7681 | 50.986 | 3.3714
Image_B200_ImageSize_128 | 87.5382 | 99.828 | 25 | 47.0926 | 79.0945 | 89.6768 | 25 | 45.9463 | 77.2446 | 45.7872 | 180000 | 74.828 | 1.258 | 1.4199 | 179947.5 | 52 | 0 | 0.5 | 87.573 | 0.039409 | 0.013 | 174641 | 1.2436 | 1.4376 | 5359 | 1.7283 | 74.828 | 87.9209 | 0.99779 | 180000 | 64.6768 | 0.26807 | 0.30248 | 179999.5 | 0 | 0 | 0.5 | 79.0965 | 0.03664 | 0.012 | 173986 | 0.26527 | 0.3062 | 6014 | 0.3491 | 64.6768 | 79.2188 | 0.79799
Image_B200_ImageSize_32 | 54.6174 | 64.1637 | 25 | 25.4798 | 50.6353 | 56.2361 | 25 | 22.0995 | 49.7457 | 21.4374 | 180000 | 39.1637 | 0.59267 | 1.1251 | 179684 | 315.5 | 0 | 0.5 | 54.6325 | 0.033576 | 0.013 | 179122.5 | 0.58134 | 1.1416 | 877.5 | 2.907 | 39.1637 | 55.5024 | 4.885 | 180000 | 31.2361 | 0.12869 | 0.24109 | 179999.5 | 0 | 0 | 0.5 | 50.6361 | 0.032488 | 0.012 | 179178.5 | 0.12674 | 0.24423 | 821.5 | 0.55363 | 31.2361 | 51.0305 | 4.8995
Image_B200_ImageSize_64 | 73.0722 | 85.8125 | 25 | 39.2499 | 66.5896 | 75.1413 | 25 | 35.3511 | 65.1643 | 34.95 | 180000 | 60.8125 | 0.96562 | 1.4943 | 179804 | 90 | 105.5 | 0.5 | 73.0986 | 0.03289 | 0.013 | 178393 | 0.95303 | 1.5127 | 1607 | 2.3637 | 60.8125 | 75.959 | 2.4896 | 180000 | 50.1413 | 0.20646 | 0.31653 | 179999.5 | 0 | 0 | 0.5 | 66.5911 | 0.029549 | 0.012 | 179190 | 0.20465 | 0.32027 | 810 | 0.60836 | 50.1413 | 68.0991 | 4.1912
Image_B200_ModelSize_128 | 54.6174 | 64.1637 | 25 | 25.4798 | 50.6353 | 56.2361 | 25 | 22.0995 | 49.7457 | 21.4374 | 180000 | 39.1637 | 0.59267 | 1.1251 | 179684 | 315.5 | 0 | 0.5 | 54.6325 | 0.033576 | 0.013 | 179122.5 | 0.58134 | 1.1416 | 877.5 | 2.907 | 39.1637 | 55.5024 | 4.885 | 180000 | 31.2361 | 0.12869 | 0.24109 | 179999.5 | 0 | 0 | 0.5 | 50.6361 | 0.032488 | 0.012 | 179178.5 | 0.12674 | 0.24423 | 821.5 | 0.55363 | 31.2361 | 51.0305 | 4.8995
Image_B200_ModelSize_256 | 58.9381 | 71.6379 | 25 | 30.8045 | 54.3654 | 61.1143 | 25 | 25.6095 | 53.3517 | 24.8381 | 180000 | 46.6379 | 0.68092 | 1.4848 | 179836.5 | 69.5 | 93.5 | 0.5 | 58.9561 | 0.032894 | 0.013 | 178970.5 | 0.67118 | 1.5159 | 1029.5 | 2.3735 | 46.6379 | 60.3345 | 4.0942 | 180003 | 36.1143 | 0.14676 | 0.31451 | 180002.5 | 0 | 0 | 0.5 | 54.3665 | 0.032298 | 0.012 | 179256.5 | 0.14519 | 0.31937 | 746.5 | 0.52308 | 36.1143 | 54.3434 | 5.4068
Image_B200_ModelSize_512 | 60.6008 | 76.3242 | 25 | 34.4439 | 55.795 | 63.7862 | 25 | 27.5802 | 54.7356 | 26.4086 | 180000 | 51.3242 | 0.71577 | 1.7617 | 179932 | 4 | 63.5 | 0.5 | 60.6202 | 0.034378 | 0.013 | 176991 | 0.695 | 1.8298 | 3009 | 1.938 | 51.3242 | 67.532 | 1.5552 | 180000 | 38.7862 | 0.15346 | 0.37052 | 179999.5 | 0 | 0 | 0.5 | 55.7961 | 0.034006 | 0.012 | 178813 | 0.1513 | 0.38339 | 1187 | 0.47836 | 38.7862 | 58.7892 | 3.6693
Image_H100_BatchSize_128 | 44.982 | 51.6142 | 25 | 17.3244 | 42.2997 | 46.1209 | 25 | 14.9379 | 41.6957 | 14.492 | 180000 | 26.6142 | 0.39908 | 0.76508 | 179980 | 19.5 | 0 | 0.5 | 44.9919 | 0.036122 | 0.013 | 179072.5 | 0.39247 | 0.7887 | 927.5 | 1.6748 | 26.6142 | 45.8172 | 5.1848 | 180000 | 21.1209 | 0.08732 | 0.16579 | 179999.5 | 0 | 0 | 0.5 | 42.3003 | 0.034963 | 0.012 | 179244.5 | 0.086191 | 0.17093 | 755.5 | 0.35522 | 21.1209 | 42.5388 | 5.9892
Image_H100_BatchSize_256 | 44.142 | 49.1012 | 25 | 15.4529 | 41.5746 | 44.9851 | 25 | 14.2033 | 40.9947 | 13.8152 | 180000 | 24.1012 | 0.38191 | 0.57939 | 179999.5 | 0 | 0 | 0.5 | 44.1513 | 0.032856 | 0.013 | 177187 | 0.37629 | 0.5906 | 2813 | 0.73594 | 24.1012 | 45.482 | 1.4689 | 180000 | 19.9851 | 0.083805 | 0.12635 | 179999.5 | 0 | 0.5 | 0 | 41.5751 | 0.032353 | 0.012 | 178596.5 | 0.083062 | 0.12831 | 1403.5 | 0.17831 | 19.9851 | 42.8678 | 2.8198
Image_H100_BatchSize_512 | 45.2066 | 54.2981 | 25 | 19.3746 | 42.4878 | 46.9963 | 25 | 15.5332 | 41.8767 | 15.0689 | 180000 | 29.2981 | 0.40453 | 1.0305 | 179844 | 155.5 | 0 | 0.5 | 45.2166 | 0.037195 | 0.013 | 177894 | 0.39348 | 1.0582 | 2106 | 1.3382 | 29.2981 | 47.0975 | 2.4035 | 180001 | 21.9963 | 0.088384 | 0.22176 | 180000.5 | 0 | 0 | 0.5 | 42.4884 | 0.037413 | 0.012 | 177865 | 0.086485 | 0.22836 | 2136 | 0.24654 | 21.9963 | 42.919 | 2.3337
Image_H100_ImageSize_16 | 40.9893 | 45.4721 | 25 | 13.1307 | 38.8465 | 41.7667 | 25 | 11.8765 | 38.3609 | 11.6389 | 180000 | 20.4721 | 0.31868 | 0.52046 | 179999.5 | 0 | 0 | 0.5 | 40.9969 | 0.034335 | 0.013 | 178370.5 | 0.31448 | 0.53055 | 1629.5 | 0.77888 | 20.4721 | 41.4129 | 2.7408 | 180000 | 16.7667 | 0.070163 | 0.11386 | 179999.5 | 0 | 0.5 | 0 | 38.847 | 0.032727 | 0.012 | 179012.5 | 0.069369 | 0.11572 | 987.5 | 0.2141 | 16.7667 | 39.3726 | 4.1433
Image_H100_ImageSize_32 | 44.982 | 51.6142 | 25 | 17.3244 | 42.2997 | 46.1209 | 25 | 14.9379 | 41.6957 | 14.492 | 180000 | 26.6142 | 0.39908 | 0.76508 | 179980 | 19.5 | 0 | 0.5 | 44.9919 | 0.036122 | 0.013 | 179072.5 | 0.39247 | 0.7887 | 927.5 | 1.6748 | 26.6142 | 45.8172 | 5.1848 | 180000 | 21.1209 | 0.08732 | 0.16579 | 179999.5 | 0 | 0 | 0.5 | 42.3003 | 0.034963 | 0.012 | 179244.5 | 0.086191 | 0.17093 | 755.5 | 0.35522 | 21.1209 | 42.5388 | 5.9892
Image_H100_ImageSize_64 | 64.0995 | 73.492 | 25 | 31.1259 | 58.8364 | 65.7104 | 25 | 28.6811 | 57.6699 | 28.4584 | 179997 | 48.492 | 0.78368 | 1.1039 | 179821.5 | 175 | 0 | 0.5 | 64.1202 | 0.034719 | 0.013 | 172886.5 | 0.76433 | 1.1446 | 7110.5 | 1.2543 | 48.492 | 66.2294 | 0.64193 | 179997 | 40.7104 | 0.16887 | 0.23626 | 179996.5 | 0 | 0 | 0.5 | 58.8376 | 0.031983 | 0.012 | 174268.5 | 0.16567 | 0.24063 | 5728.5 | 0.2661 | 40.7104 | 62.4487 | 0.68332
Image_H100_ModelSize_128 | 44.982 | 51.6142 | 25 | 17.3244 | 42.2997 | 46.1209 | 25 | 14.9379 | 41.6957 | 14.492 | 180000 | 26.6142 | 0.39908 | 0.76508 | 179980 | 19.5 | 0 | 0.5 | 44.9919 | 0.036122 | 0.013 | 179072.5 | 0.39247 | 0.7887 | 927.5 | 1.6748 | 26.6142 | 45.8172 | 5.1848 | 180000 | 21.1209 | 0.08732 | 0.16579 | 179999.5 | 0 | 0 | 0.5 | 42.3003 | 0.034963 | 0.012 | 179244.5 | 0.086191 | 0.17093 | 755.5 | 0.35522 | 21.1209 | 42.5388 | 5.9892
Image_H100_ModelSize_256 | 49.7624 | 58.9339 | 25 | 22.6099 | 46.4309 | 51.4222 | 25 | 18.5264 | 45.6869 | 18.2842 | 179997 | 33.9339 | 0.49593 | 1.0582 | 179869.5 | 127 | 0 | 0.5 | 49.775 | 0.03401 | 0.013 | 178498.5 | 0.4869 | 1.0955 | 1498.5 | 1.5711 | 33.9339 | 53.522 | 2.9202 | 180000 | 26.4222 | 0.10763 | 0.22694 | 179999.5 | 0 | 0 | 0.5 | 46.4316 | 0.033334 | 0.012 | 179614.5 | 0.10656 | 0.23151 | 385.5 | 0.60907 | 26.4222 | 46.5714 | 10.8728
Image_H100_ModelSize_512 | 50.6219 | 61.9045 | 25 | 24.9589 | 47.1738 | 53.0469 | 25 | 19.1811 | 46.4069 | 18.2834 | 180000 | 36.9045 | 0.51339 | 1.2422 | 179955.5 | 14.5 | 29.5 | 0.5 | 50.6353 | 0.035225 | 0.013 | 177922.5 | 0.50237 | 1.2556 | 2077.5 | 1.4573 | 36.9045 | 55.6942 | 2.3408 | 180000 | 28.0469 | 0.11099 | 0.26505 | 179999.5 | 0 | 0 | 0.5 | 47.1746 | 0.033735 | 0.012 | 179492.5 | 0.10998 | 0.27323 | 507.5 | 0.46839 | 28.0469 | 49.7492 | 8.479
Text_B200_BatchSize16 | 92.7371 | 109.5892 | 25 | 51.9234 | 83.6374 | 96.6034 | 25 | 49.8905 | 81.6533 | 49.568 | 180000 | 84.5892 | 1.3559 | 1.7888 | 179600 | 4 | 395.5 | 0.5 | 92.7755 | 0.036427 | 0.013 | 177207 | 1.3253 | 1.8783 | 2793 | 3.2966 | 84.5892 | 94.4033 | 1.702 | 180000 | 71.6034 | 0.28739 | 0.37659 | 179996 | 3.5 | 0 | 0.5 | 83.6396 | 0.034384 | 0.012 | 177234 | 0.28186 | 0.39376 | 2766 | 0.64209 | 71.6034 | 84.23 | 1.5661
Text_B200_BatchSize2 | 60.461 | 67.5105 | 25 | 26.1716 | 55.6929 | 61.9268 | 25 | 25.9545 | 54.6272 | 25.7407 | 180000 | 42.5105 | 0.70967 | 0.77549 | 179998 | 1.5 | 0 | 0.5 | 60.4791 | 0.039261 | 0.013 | 177422.5 | 0.70587 | 0.8093 | 2577.5 | 0.97138 | 42.5105 | 60.799 | 1.9892 | 180000 | 36.9268 | 0.15416 | 0.16815 | 179999.5 | 0 | 0 | 0.5 | 55.6939 | 0.033046 | 0.012 | 177636.5 | 0.15344 | 0.17534 | 2363.5 | 0.20862 | 36.9268 | 57.1797 | 1.6607
Text_B200_BatchSize32 | 99.6934 | 115.8579 | 25 | 56.9342 | 89.5851 | 102.1818 | 25 | 54.6192 | 87.3901 | 54.0141 | 180000 | 90.8579 | 1.5067 | 1.8775 | 179576.5 | 23.5 | 399.5 | 0.5 | 99.7366 | 0.040316 | 0.013 | 177509.5 | 1.4702 | 1.9571 | 2490.5 | 4.1035 | 90.8579 | 100.9629 | 2.1883 | 180000 | 77.1818 | 0.31837 | 0.39458 | 179999.5 | 0 | 0 | 0.5 | 89.5876 | 0.037242 | 0.012 | 177446.5 | 0.3119 | 0.41124 | 2553.5 | 0.76829 | 77.1818 | 90.5515 | 1.9035
Text_B200_Deepspeedds_z1 | 89.6117 | 107.9142 | 25 | 49.8144 | 80.9528 | 94.336 | 25 | 47.584 | 79.0629 | 47.2348 | 180000 | 82.9142 | 1.2902 | 1.8752 | 179583.5 | 5 | 409.5 | 2 | 89.6481 | 0.035808 | 0.013 | 177909.5 | 1.248 | 1.9656 | 2090.5 | 4.8802 | 82.9142 | 91.0528 | 2.2796 | 180000 | 69.336 | 0.27365 | 0.39568 | 179996 | 3.5 | 0 | 0.5 | 80.9549 | 0.034169 | 0.012 | 177918.5 | 0.26609 | 0.41347 | 2081.5 | 0.91997 | 69.336 | 80.8026 | 2.1211
Text_B200_Deepspeedds_z2 | 91.5437 | 108.0457 | 25 | 51.1416 | 82.5945 | 95.0856 | 25 | 48.9231 | 80.6424 | 48.5051 | 180000 | 83.0457 | 1.3335 | 1.776 | 179592 | 12 | 395.5 | 0.5 | 91.5814 | 0.037927 | 0.013 | 177247 | 1.3026 | 1.8785 | 2753 | 3.3208 | 83.0457 | 93.031 | 1.8174 | 180000 | 70.0856 | 0.28279 | 0.3741 | 179997 | 2.5 | 0 | 0.5 | 82.5967 | 0.0348 | 0.012 | 177324 | 0.27723 | 0.39476 | 2676 | 0.65124 | 70.0856 | 82.9644 | 1.6377
Text_B200_Deepspeedds_z3 | 92.7371 | 109.5892 | 25 | 51.9234 | 83.6374 | 96.6034 | 25 | 49.8905 | 81.6533 | 49.568 | 180000 | 84.5892 | 1.3559 | 1.7888 | 179600 | 4 | 395.5 | 0.5 | 92.7755 | 0.036427 | 0.013 | 177207 | 1.3253 | 1.8783 | 2793 | 3.2966 | 84.5892 | 94.4033 | 1.702 | 180000 | 71.6034 | 0.28739 | 0.37659 | 179996 | 3.5 | 0 | 0.5 | 83.6396 | 0.034384 | 0.012 | 177234 | 0.28186 | 0.39376 | 2766 | 0.64209 | 71.6034 | 84.23 | 1.5661
Text_B200_Lamma_1B | 62.794 | 73.0262 | 25 | 30.4597 | 57.7067 | 64.4577 | 25 | 27.8954 | 56.5757 | 27.393 | 180000 | 48.0262 | 0.75738 | 1.1927 | 179208 | 791.5 | 0 | 0.5 | 62.8138 | 0.03478 | 0.013 | 178971.5 | 0.72836 | 1.2377 | 1028.5 | 5.8069 | 48.0262 | 63.6511 | 4.4245 | 180000 | 39.4577 | 0.16368 | 0.25552 | 179999.5 | 0 | 0 | 0.5 | 57.7078 | 0.032385 | 0.012 | 178995.5 | 0.15849 | 0.26523 | 1004.5 | 1.0897 | 39.4577 | 58.2073 | 4.0553
Text_B200_Lamma_3B | 74.2053 | 87.3781 | 25 | 38.8831 | 67.576 | 76.6185 | 25 | 36.032 | 66.1161 | 35.6066 | 180000 | 62.3781 | 0.98743 | 1.4873 | 179480.5 | 509 | 10 | 0.5 | 74.2322 | 0.035007 | 0.013 | 178237.5 | 0.95861 | 1.5784 | 1762.5 | 3.9024 | 62.3781 | 76.4345 | 2.593 | 180000 | 51.6185 | 0.21144 | 0.31569 | 179999.5 | 0 | 0 | 0.5 | 67.5776 | 0.033181 | 0.012 | 178249.5 | 0.20626 | 0.33443 | 1750.5 | 0.7385 | 51.6185 | 68.1777 | 2.385
Text_B200_Lamma_8B | 92.7371 | 109.5892 | 25 | 51.9234 | 83.6374 | 96.6034 | 25 | 49.8905 | 81.6533 | 49.568 | 180000 | 84.5892 | 1.3559 | 1.7888 | 179600 | 4 | 395.5 | 0.5 | 92.7755 | 0.036427 | 0.013 | 177207 | 1.3253 | 1.8783 | 2793 | 3.2966 | 84.5892 | 94.4033 | 1.702 | 180000 | 71.6034 | 0.28739 | 0.37659 | 179996 | 3.5 | 0 | 0.5 | 83.6396 | 0.034384 | 0.012 | 177234 | 0.28186 | 0.39376 | 2766 | 0.64209 | 71.6034 | 84.23 | 1.5661
Text_B200_SeqLength_1024 | 92.5375 | 108.7878 | 25 | 51.9414 | 83.443 | 95.8617 | 25 | 49.5812 | 81.4605 | 49.214 | 180000 | 83.7878 | 1.3552 | 1.7883 | 179596 | 8 | 395.5 | 0.5 | 92.5758 | 0.03696 | 0.013 | 177194 | 1.3243 | 1.8815 | 2806 | 3.3033 | 83.7878 | 94.2073 | 1.7308 | 180000 | 70.8617 | 0.28726 | 0.37655 | 179997 | 2.5 | 0 | 0.5 | 83.4452 | 0.035015 | 0.012 | 177168 | 0.28167 | 0.39577 | 2832 | 0.63693 | 70.8617 | 84.1816 | 1.5717
Text_B200_SeqLength_2048 | 92.7371 | 109.5892 | 25 | 51.9234 | 83.6374 | 96.6034 | 25 | 49.8905 | 81.6533 | 49.568 | 180000 | 84.5892 | 1.3559 | 1.7888 | 179600 | 4 | 395.5 | 0.5 | 92.7755 | 0.036427 | 0.013 | 177207 | 1.3253 | 1.8783 | 2793 | 3.2966 | 84.5892 | 94.4033 | 1.702 | 180000 | 71.6034 | 0.28739 | 0.37659 | 179996 | 3.5 | 0 | 0.5 | 83.6396 | 0.034384 | 0.012 | 177234 | 0.28186 | 0.39376 | 2766 | 0.64209 | 71.6034 | 84.23 | 1.5661
Text_B200_SeqLength_4096 | 92.6408 | 109.184 | 25 | 51.9826 | 83.5368 | 96.1343 | 25 | 49.7394 | 81.5522 | 49.2714 | 180000 | 84.184 | 1.3566 | 1.7903 | 179597 | 7 | 395.5 | 0.5 | 92.6792 | 0.037406 | 0.013 | 177220 | 1.3259 | 1.8627 | 2780 | 3.3149 | 84.184 | 94.3808 | 1.7762 | 180000 | 71.1343 | 0.28754 | 0.37691 | 179997 | 2.5 | 0 | 0.5 | 83.539 | 0.03431 | 0.012 | 177200 | 0.28198 | 0.39129 | 2800 | 0.63976 | 71.1343 | 84.1997 | 1.5434
Text_H100_BatchSize16 | 76.7072 | 87.6299 | 25 | 39.2423 | 69.7341 | 78.364 | 25 | 37.8268 | 68.1964 | 37.3445 | 180000 | 62.6299 | 1.0386 | 1.2649 | 179731.5 | 268 | 0 | 0.5 | 76.7353 | 0.039707 | 0.013 | 177094 | 1.0175 | 1.3293 | 2906 | 2.3253 | 62.6299 | 77.5304 | 1.8423 | 180000 | 53.364 | 0.22272 | 0.27023 | 179999.5 | 0 | 0 | 0.5 | 69.7357 | 0.037676 | 0.012 | 177072 | 0.21889 | 0.28515 | 2928 | 0.45442 | 53.364 | 69.9006 | 1.6865
Text_H100_BatchSize2 | 49.8527 | 55.0906 | 25 | 18.3533 | 46.5228 | 51.0233 | 25 | 18.118 | 45.7723 | 18.0853 | 180000 | 30.0906 | 0.49539 | 0.55374 | 179999.5 | 0 | 0 | 0.5 | 49.8649 | 0.040238 | 0.013 | 176935 | 0.49197 | 0.59395 | 3065 | 0.69287 | 30.0906 | 50.0097 | 1.75 | 180000 | 26.0233 | 0.10846 | 0.12106 | 179999.5 | 0 | 0 | 0.5 | 46.5235 | 0.034423 | 0.012 | 176998 | 0.1078 | 0.12997 | 3002 | 0.14726 | 26.0233 | 46.9779 | 1.4149
Text_H100_BatchSize32 | 79.2422 | 90.618 | 25 | 41.111 | 71.9238 | 81.0042 | 25 | 39.6778 | 70.3123 | 39.3124 | 180000 | 65.618 | 1.0901 | 1.3083 | 179748.5 | 251 | 0 | 0.5 | 79.2718 | 0.041842 | 0.013 | 177469.5 | 1.0691 | 1.3656 | 2530.5 | 2.5628 | 65.618 | 80.0875 | 2.2432 | 180000 | 56.0042 | 0.23343 | 0.27917 | 179999.5 | 0 | 0 | 0.5 | 71.9255 | 0.037128 | 0.012 | 177498.5 | 0.22963 | 0.29123 | 2501.5 | 0.5032 | 56.0042 | 72.3313 | 1.9317
Text_H100_Deepspeedds_z1 | 73.2022 | 84.9304 | 25 | 37.7598 | 66.706 | 75.1642 | 25 | 35.3337 | 65.2728 | 34.7956 | 180000 | 59.9304 | 0.96752 | 1.3799 | 179414.5 | 582.5 | 2.5 | 0.5 | 73.2283 | 0.037283 | 0.013 | 178618.5 | 0.93195 | 1.398 | 1381.5 | 5.5673 | 59.9304 | 73.8655 | 3.5946 | 180000 | 50.1642 | 0.20755 | 0.29377 | 179999.5 | 0 | 0 | 0.5 | 66.7075 | 0.036666 | 0.012 | 178618.5 | 0.20116 | 0.29783 | 1381.5 | 1.0346 | 50.1642 | 66.7835 | 3.4955
Text_H100_Deepspeedds_z2 | 75.2307 | 86.1897 | 25 | 38.1622 | 68.4588 | 76.9483 | 25 | 36.6978 | 66.9642 | 36.4328 | 180000 | 61.1897 | 1.0085 | 1.2456 | 179720 | 279.5 | 0 | 0.5 | 75.2579 | 0.041834 | 0.013 | 176893 | 0.98608 | 1.3472 | 3107 | 2.2866 | 61.1897 | 76.2168 | 1.8476 | 180000 | 51.9483 | 0.21645 | 0.26635 | 179999.5 | 0 | 0 | 0.5 | 68.4604 | 0.03727 | 0.012 | 176879 | 0.21238 | 0.28271 | 3121 | 0.44749 | 51.9483 | 68.6529 | 1.5601
Text_H100_Deepspeedds_z3 | 76.7072 | 87.6299 | 25 | 39.2423 | 69.7341 | 78.364 | 25 | 37.8268 | 68.1964 | 37.3445 | 180000 | 62.6299 | 1.0386 | 1.2649 | 179731.5 | 268 | 0 | 0.5 | 76.7353 | 0.039707 | 0.013 | 177094 | 1.0175 | 1.3293 | 2906 | 2.3253 | 62.6299 | 77.5304 | 1.8423 | 180000 | 53.364 | 0.22272 | 0.27023 | 179999.5 | 0 | 0 | 0.5 | 69.7357 | 0.037676 | 0.012 | 177072 | 0.21889 | 0.28515 | 2928 | 0.45442 | 53.364 | 69.9006 | 1.6865
Text_H100_Lamma_1B | 56.4937 | 65.5312 | 25 | 25.6554 | 52.259 | 58.0945 | 25 | 23.1757 | 51.3141 | 22.8234 | 180000 | 40.5312 | 0.63035 | 1.0421 | 179288.5 | 711 | 0 | 0.5 | 56.5099 | 0.034457 | 0.013 | 178779.5 | 0.60383 | 1.0969 | 1220.5 | 4.5152 | 40.5312 | 57.8819 | 3.6735 | 180000 | 33.0945 | 0.13671 | 0.22426 | 179999.5 | 0 | 0 | 0.5 | 52.2599 | 0.033183 | 0.012 | 178758.5 | 0.13189 | 0.23418 | 1241.5 | 0.83026 | 33.0945 | 52.7977 | 3.3929
Text_H100_Lamma_3B | 67.6084 | 78.1174 | 25 | 33.1706 | 61.8782 | 69.4999 | 25 | 31.2109 | 60.6089 | 30.794 | 180000 | 53.1174 | 0.85325 | 1.187 | 179571.5 | 428 | 0 | 0.5 | 67.6311 | 0.036226 | 0.013 | 177418.5 | 0.83103 | 1.2444 | 2581.5 | 2.3803 | 53.1174 | 69.0354 | 1.8306 | 180000 | 44.4999 | 0.18372 | 0.25411 | 179999.5 | 0 | 0 | 0.5 | 61.8796 | 0.034527 | 0.012 | 177414.5 | 0.17966 | 0.26644 | 2585.5 | 0.462 | 44.4999 | 62.45 | 1.6871
Text_H100_Lamma_8B | 76.7072 | 87.6299 | 25 | 39.2423 | 69.7341 | 78.364 | 25 | 37.8268 | 68.1964 | 37.3445 | 180000 | 62.6299 | 1.0386 | 1.2649 | 179731.5 | 268 | 0 | 0.5 | 76.7353 | 0.039707 | 0.013 | 177094 | 1.0175 | 1.3293 | 2906 | 2.3253 | 62.6299 | 77.5304 | 1.8423 | 180000 | 53.364 | 0.22272 | 0.27023 | 179999.5 | 0 | 0 | 0.5 | 69.7357 | 0.037676 | 0.012 | 177072 | 0.21889 | 0.28515 | 2928 | 0.45442 | 53.364 | 69.9006 | 1.6865
Text_H100_SeqLength_1024 | 76.683 | 87.6407 | 25 | 39.2837 | 69.7137 | 78.4767 | 25 | 37.9524 | 68.1768 | 37.5875 | 180000 | 62.6407 | 1.038 | 1.2642 | 179727.5 | 272 | 0 | 0.5 | 76.711 | 0.041023 | 0.013 | 177113.5 | 1.0166 | 1.3363 | 2886.5 | 2.3511 | 62.6407 | 77.3852 | 1.9369 | 180000 | 53.4767 | 0.2226 | 0.27008 | 179999.5 | 0 | 0 | 0.5 | 69.7153 | 0.03673 | 0.012 | 177091.5 | 0.21872 | 0.2851 | 2908.5 | 0.45897 | 53.4767 | 70.0353 | 1.6404
Text_H100_SeqLength_2048 | 76.7072 | 87.6299 | 25 | 39.2423 | 69.7341 | 78.364 | 25 | 37.8268 | 68.1964 | 37.3445 | 180000 | 62.6299 | 1.0386 | 1.2649 | 179731.5 | 268 | 0 | 0.5 | 76.7353 | 0.039707 | 0.013 | 177094 | 1.0175 | 1.3293 | 2906 | 2.3253 | 62.6299 | 77.5304 | 1.8423 | 180000 | 53.364 | 0.22272 | 0.27023 | 179999.5 | 0 | 0 | 0.5 | 69.7357 | 0.037676 | 0.012 | 177072 | 0.21889 | 0.28515 | 2928 | 0.45442 | 53.364 | 69.9006 | 1.6865
Text_H100_SeqLength_4096 | 76.5573 | 87.5261 | 25 | 39.1376 | 69.6049 | 78.2451 | 25 | 37.7379 | 68.0717 | 37.2868 | 180000 | 62.5261 | 1.0355 | 1.2643 | 179731.5 | 268 | 0 | 0.5 | 76.5853 | 0.039373 | 0.013 | 177119 | 1.0141 | 1.3331 | 2881 | 2.3488 | 62.5261 | 77.3395 | 1.838 | 180000 | 53.2451 | 0.22207 | 0.27011 | 179999.5 | 0 | 0 | 0.5 | 69.6065 | 0.036838 | 0.012 | 177087 | 0.21819 | 0.28444 | 2913 | 0.45796 | 53.2451 | 69.9407 | 1.6454

## Nf_results
scenario | IGBT_Nf_eq | IGBT_Nf_eq_dT_ge10 | IGBT_Nf_eq_dT_lt10 | IGBT_Nf_eq_load_cycles | IGBT_Nf_eq_grid_cycles | IGBT_Nf_worst_cycle | IGBT_worst_cycle_dT_K | IGBT_worst_cycle_Tmean_C | Diode_Nf_eq | Diode_Nf_eq_dT_ge10 | Diode_Nf_eq_dT_lt10 | Diode_Nf_eq_load_cycles | Diode_Nf_eq_grid_cycles | Diode_Nf_worst_cycle | Diode_worst_cycle_dT_K | Diode_worst_cycle_Tmean_C | Limiting_device
Image_B200_BatchSize_128 | 23127076.4102 | 23127079.6506 | 1.6506e+14 | 23127076.4102 | 1.6863e+27 | 11563539.8253 | 39.1637 | 44.5819 | 66347847.8098 | 66347847.8098 | 1.1502e+27 | 66347847.8098 | 5.5628e+37 | 33173923.9049 | 31.2361 | 40.618 | IGBT
Image_B200_BatchSize_256 | 18030188.2289 | 18030244.316 | 5.7961e+12 | 18030188.2289 | 1.9239e+26 | 9015122.158 | 40.5994 | 45.2997 | 63366413.0517 | 63366413.0517 | 5.3078e+25 | 63366413.0517 | 8.5744e+36 | 31683206.5259 | 31.4065 | 40.7033 | IGBT
Image_B200_BatchSize_512 | 14705205.1069 | 14705509.6186 | 710145269513.2117 | 14705205.1069 | 4.9301e+25 | 7352754.8093 | 41.8449 | 45.9224 | 57534892.9703 | 57534892.9703 | 6.7499e+24 | 57534892.9703 | 2.6693e+36 | 28767446.4851 | 31.7681 | 40.8841 | IGBT
Image_B200_ImageSize_128 | 514330.986 | 514331.1842 | 1.3352e+12 | 514330.986 | 5.6585e+24 | 257165.5921 | 74.828 | 62.414 | 564872.3088 | 564872.3088 | 1.0818e+24 | 564872.3088 | 2.7004e+35 | 282436.1544 | 64.6768 | 57.3384 | IGBT
Image_B200_ImageSize_32 | 23127076.4102 | 23127079.6506 | 1.6506e+14 | 23127076.4102 | 1.6863e+27 | 11563539.8253 | 39.1637 | 44.5819 | 66347847.8098 | 66347847.8098 | 1.1502e+27 | 66347847.8098 | 5.5628e+37 | 33173923.9049 | 31.2361 | 40.618 | IGBT
Image_B200_ImageSize_64 | 1581800.1635 | 1581803.5613 | 736384634815.1031 | 1581800.1635 | 3.8163e+24 | 790905.4053 | 60.8125 | 55.4063 | 2367379.9691 | 2367379.9691 | 8.8301e+23 | 2367379.9691 | 2.2258e+35 | 1183689.9846 | 50.1413 | 50.0706 | IGBT
Image_B200_ModelSize_128 | 23127076.4102 | 23127079.6506 | 1.6506e+14 | 23127076.4102 | 1.6863e+27 | 11563539.8253 | 39.1637 | 44.5819 | 66347847.8098 | 66347847.8098 | 1.1502e+27 | 66347847.8098 | 5.5628e+37 | 33173923.9049 | 31.2361 | 40.618 | IGBT
Image_B200_ModelSize_256 | 7338177.8803 | 7338218.6834 | 1.3197e+12 | 7338177.8803 | 1.1768e+25 | 3669162.3599 | 46.6379 | 48.3189 | 20818743.4831 | 20818743.4831 | 1.1686e+24 | 20818743.4831 | 7.1384e+35 | 10409371.7416 | 36.1143 | 43.0572 | IGBT
Image_B200_ModelSize_512 | 4125891.1693 | 4125891.1803 | 1544733548878902 | 4125891.1693 | 6.7088e+23 | 2063741.2796 | 51.3242 | 50.6621 | 12378602.1159 | 12378602.1159 | 3.6459e+20 | 12378602.1159 | 4.7975e+34 | 6189301.0579 | 38.7862 | 44.3931 | IGBT
Image_H100_BatchSize_128 | 570865375.1383 | 570865377.807 | 1.2212e+17 | 570865375.1383 | 1.319e+30 | 285432688.9035 | 26.6142 | 38.3071 | 3376395114.1011 | 3376395114.1011 | 2.4468e+29 | 3376395114.1011 | 2.1791e+40 | 1688197557.0506 | 21.1209 | 35.5604 | IGBT
Image_H100_BatchSize_256 | 1561833111.7123 | 1561833111.7279 | 1.5635e+20 | 1561833111.7123 | 7.6219e+31 | 780916555.864 | 24.1012 | 37.0506 | 6505456101.3967 | 6505456101.3967 | 9.4955e+31 | 6505456101.3967 | 8.0881e+41 | 3252728050.6984 | 19.9851 | 34.9925 | IGBT
Image_H100_BatchSize_512 | 232260918.3973 | 232261189.957 | 1.9865e+14 | 232260918.3973 | 2.0231e+28 | 116130594.9785 | 29.2981 | 39.6491 | 2119097597.4414 | 2119097597.4414 | 4.1938e+26 | 2119097597.4414 | 5.1493e+38 | 1059548798.7207 | 21.9963 | 35.9982 | IGBT
Image_H100_ImageSize_16 | 9747139663.6897 | 9747139663.7169 | 3.4947e+21 | 9747139663.6897 | 7.9343e+32 | 4873569831.8585 | 20.4721 | 35.2361 | 61276298010.36 | 61276298010.36 | 3.1124e+33 | 61276298010.36 | 7.6318e+42 | 30638149005.18 | 16.7667 | 33.3834 | IGBT
Image_H100_ImageSize_32 | 570865375.1383 | 570865377.807 | 1.2212e+17 | 570865375.1383 | 1.319e+30 | 285432688.9035 | 26.6142 | 38.3071 | 3376395114.1011 | 3376395114.1011 | 2.4468e+29 | 3376395114.1011 | 2.1791e+40 | 1688197557.0506 | 21.1209 | 35.5604 | IGBT
Image_H100_ImageSize_64 | 5782616.8648 | 5782618.0449 | 2.8336e+13 | 5782616.8648 | 9.2426e+26 | 2891309.0224 | 48.492 | 49.246 | 8847838.8297 | 8847838.8297 | 4.5981e+25 | 8847838.8297 | 2.5788e+37 | 4423919.4148 | 40.7104 | 45.3552 | IGBT
Image_H100_ModelSize_128 | 570865375.1383 | 570865377.807 | 1.2212e+17 | 570865375.1383 | 1.319e+30 | 285432688.9035 | 26.6142 | 38.3071 | 3376395114.1011 | 3376395114.1011 | 2.4468e+29 | 3376395114.1011 | 2.1791e+40 | 1688197557.0506 | 21.1209 | 35.5604 | IGBT
Image_H100_ModelSize_256 | 67262877.4085 | 67262946.019 | 6.5942e+13 | 67262877.4085 | 3.8804e+27 | 33631473.0095 | 33.9339 | 41.967 | 306360724.4527 | 306360724.4527 | 4.0673e+25 | 306360724.4527 | 1.1417e+38 | 153180362.2264 | 26.4222 | 38.2111 | IGBT
Image_H100_ModelSize_512 | 35444410.7341 | 35444506.9231 | 1.3061e+13 | 35444410.7341 | 3.2657e+26 | 17722681.7238 | 36.9045 | 43.4523 | 173163778.7422 | 173163778.7422 | 3.7051e+21 | 173163778.7422 | 1.0328e+37 | 86581889.3711 | 28.0469 | 39.0234 | IGBT
Text_B200_BatchSize16 | 264946.339 | 264946.3391 | 3514479585408696 | 264946.339 | 1.5473e+23 | 132496.2595 | 84.5892 | 67.2946 | 325975.1852 | 325975.1853 | 2387330686108966 | 325975.1852 | 1.2479e+34 | 162987.5926 | 71.6034 | 60.8017 | IGBT
Text_B200_BatchSize2 | 13249410.8128 | 13249410.8129 | 2.2516e+18 | 13249410.8128 | 2.8502e+29 | 6624705.4064 | 42.5105 | 46.2552 | 17647486.2554 | 17647486.2554 | 1.4419e+26 | 17647486.2554 | 4.4228e+39 | 8823743.1277 | 36.9268 | 43.4634 | IGBT
Text_B200_BatchSize32 | 179267.5469 | 179267.5476 | 4.6476e+13 | 179267.5469 | 5.4955e+22 | 89642.4689 | 90.8579 | 70.4289 | 217586.1085 | 217586.1085 | 1.3256e+22 | 217586.1085 | 4.9293e+33 | 108793.0542 | 77.1818 | 63.5909 | IGBT
Text_B200_Deepspeedds_z1 | 295141.0581 | 295141.0581 | 3106485508408247 | 295141.0581 | 1.2831e+23 | 147705.3449 | 82.9142 | 66.4571 | 387709.053 | 387709.0575 | 3.3576e+13 | 387709.053 | 1.1219e+34 | 193854.5287 | 69.336 | 59.668 | IGBT
Text_B200_Deepspeedds_z2 | 292857.2758 | 292857.2786 | 3.0561e+13 | 292857.2758 | 1.8217e+23 | 146444.2157 | 83.0457 | 66.5229 | 365858.4491 | 365858.4491 | 29256981870388480 | 365858.4491 | 1.4455e+34 | 182929.2245 | 70.0856 | 60.0428 | IGBT
Text_B200_Deepspeedds_z3 | 264946.339 | 264946.3391 | 3514479585408696 | 264946.339 | 1.5473e+23 | 132496.2595 | 84.5892 | 67.2946 | 325975.1852 | 325975.1853 | 2387330686108966 | 325975.1852 | 1.2479e+34 | 162987.5926 | 71.6034 | 60.8017 | IGBT
Text_B200_Lamma_1B | 6132192.7229 | 6132194.2522 | 2.4589e+13 | 6132192.7229 | 5.5541e+26 | 3066097.1261 | 48.0262 | 49.0131 | 10975371.1343 | 10975371.1343 | 1.3687e+26 | 10975371.1343 | 1.9129e+37 | 5487685.5672 | 39.4577 | 44.7289 | IGBT
Text_B200_Lamma_3B | 1376138.1486 | 1376148.0935 | 190424353652.7401 | 1376138.1486 | 7.007e+24 | 688074.9638 | 62.3781 | 56.189 | 1995839.89 | 1995839.89 | 3.3881e+21 | 1995839.89 | 3.7945e+35 | 997919.945 | 51.6185 | 50.8093 | IGBT
Text_B200_Lamma_8B | 264946.339 | 264946.3391 | 3514479585408696 | 264946.339 | 1.5473e+23 | 132496.2595 | 84.5892 | 67.2946 | 325975.1852 | 325975.1853 | 2387330686108966 | 325975.1852 | 1.2479e+34 | 162987.5926 | 71.6034 | 60.8017 | IGBT
Text_B200_SeqLength_1024 | 279036.886 | 279036.886 | 59709794879900968 | 279036.886 | 1.5783e+23 | 139530.8919 | 83.7878 | 66.8939 | 344778.1838 | 344778.1838 | 3.4483e+17 | 344778.1838 | 1.2714e+34 | 172389.0919 | 70.8617 | 60.4309 | IGBT
Text_B200_SeqLength_2048 | 264946.339 | 264946.3391 | 3514479585408696 | 264946.339 | 1.5473e+23 | 132496.2595 | 84.5892 | 67.2946 | 325975.1852 | 325975.1853 | 2387330686108966 | 325975.1852 | 1.2479e+34 | 162987.5926 | 71.6034 | 60.8017 | IGBT
Text_B200_SeqLength_4096 | 271971.3384 | 271971.3384 | 22967122419626672 | 271971.3384 | 1.5486e+23 | 135999.5707 | 84.184 | 67.092 | 337721.6537 | 337721.6537 | 79922704799301968 | 337721.6537 | 1.2506e+34 | 168860.8269 | 71.1343 | 60.5671 | IGBT
Text_H100_BatchSize16 | 1346278.3169 | 1346279.7245 | 1.2876e+12 | 1346278.3169 | 8.7902e+25 | 673139.8622 | 62.6299 | 56.315 | 1646094.6411 | 1646094.6411 | 1.1343e+25 | 1646094.6411 | 3.2069e+36 | 823047.3205 | 53.364 | 51.682 | IGBT
Text_H100_BatchSize2 | 183283401.1394 | 183283401.1397 | 1.1407e+20 | 183283401.1394 | 1.1568e+32 | 91641700.5699 | 30.0906 | 40.0453 | 355988723.0813 | 355988723.0813 | 1.9266e+27 | 355988723.0813 | 1.124e+42 | 177994361.5407 | 26.0233 | 38.0117 | IGBT
Text_H100_BatchSize32 | 1044555.5959 | 1044557.3201 | 632824508304.4346 | 1044555.5959 | 4.4368e+25 | 522278.66 | 65.618 | 57.809 | 1250558.3221 | 1250558.3221 | 5.7949e+24 | 1250558.3221 | 1.7715e+36 | 625279.161 | 56.0042 | 53.0021 | IGBT
Text_H100_Deepspeedds_z1 | 1714615.1015 | 1714626.712 | 253214142115.5431 | 1714615.1015 | 3.0534e+25 | 857313.4761 | 59.9304 | 54.9652 | 2361243.23 | 2361243.23 | 1.4759e+24 | 2361243.23 | 1.4036e+36 | 1180621.615 | 50.1642 | 50.0821 | IGBT
Text_H100_Deepspeedds_z2 | 1529210.0278 | 1529211.4818 | 1.6084e+12 | 1529210.0278 | 1.2826e+26 | 764605.7409 | 61.1897 | 55.5949 | 1923200.4607 | 1923200.4607 | 1.286e+25 | 1923200.4607 | 4.5154e+36 | 961600.2303 | 51.9483 | 50.9742 | IGBT
Text_H100_Deepspeedds_z3 | 1346278.3169 | 1346279.7245 | 1.2876e+12 | 1346278.3169 | 8.7902e+25 | 673139.8622 | 62.6299 | 56.315 | 1646094.6411 | 1646094.6411 | 1.1343e+25 | 1646094.6411 | 3.2069e+36 | 823047.3205 | 53.364 | 51.682 | IGBT
Text_H100_Lamma_1B | 18239609.4076 | 18239615.7808 | 5.22e+13 | 18239609.4076 | 5.7652e+27 | 9119807.8904 | 40.5312 | 45.2656 | 41099767.0228 | 41099767.0228 | 1.4166e+26 | 41099767.0228 | 1.5417e+38 | 20549883.5114 | 33.0945 | 41.5472 | IGBT
Text_H100_Lamma_3B | 3381057.0717 | 3381060.2673 | 3.5772e+12 | 3381057.0717 | 3.3856e+26 | 1690530.1337 | 53.1174 | 51.5587 | 4924888.7433 | 4924888.7433 | 6.4356e+23 | 4924888.7433 | 1.124e+37 | 2462444.3717 | 44.4999 | 47.2499 | IGBT
Text_H100_Lamma_8B | 1346278.3169 | 1346279.7245 | 1.2876e+12 | 1346278.3169 | 8.7902e+25 | 673139.8622 | 62.6299 | 56.315 | 1646094.6411 | 1646094.6411 | 1.1343e+25 | 1646094.6411 | 3.2069e+36 | 823047.3205 | 53.364 | 51.682 | IGBT
Text_H100_SeqLength_1024 | 1344812.9423 | 1344814.3316 | 1.3018e+12 | 1344812.9423 | 8.8971e+25 | 672407.1658 | 62.6407 | 56.3204 | 1626279.0104 | 1626279.0104 | 1.1368e+25 | 1626279.0104 | 3.2467e+36 | 813139.5052 | 53.4767 | 51.7383 | IGBT
Text_H100_SeqLength_2048 | 1346278.3169 | 1346279.7245 | 1.2876e+12 | 1346278.3169 | 8.7902e+25 | 673139.8622 | 62.6299 | 56.315 | 1646094.6411 | 1646094.6411 | 1.1343e+25 | 1646094.6411 | 3.2069e+36 | 823047.3205 | 53.364 | 51.682 | IGBT
Text_H100_SeqLength_4096 | 1358536.3843 | 1358537.813 | 1.2918e+12 | 1358536.3843 | 8.9341e+25 | 679268.9065 | 62.5261 | 56.2631 | 1667358.6093 | 1667358.6093 | 1.1322e+25 | 1667358.6093 | 3.2632e+36 | 833679.3046 | 53.2451 | 51.6225 | IGBT